DIVISION 28 23 23 VT/VR9930WDM SERIES – FIBER OPTIC

TRANSMITTER AND RECEIVER

ENGINEERING SPECIFICATIONS

PART 1 - GENERAL

SUMMARY

A.   Fiber Optic FM Video Transmitter and Receiver with Bi-directional Data

SECTION INCLUDES

VT/VR9930WDM Series FM Video with Bi- directional Data – Standalone

VT/ VR9930WDM -R3 Series FM Video with

Bi-directional Data - Rack Mount

REFERENCES

Underwriters Laboratory (UL)

Underwriters Laboratory Canada (ULC)

European Union Compliance (CE)

SYSTEM DESCRIPTION

Performance Requirements: Provide a FM Video Transmitter /Receiver and integrated data transceiver system that transmits One-way video and Bi-directional RS-232, RS-422, and 2-wire RS-485.

The system shall utilize integrated WDM optics operating at 1300/1550nm capable of

simultaneous video and data transmission on

one single mode optical fiber. (VT/VR9930WDM)

SUBMITTALS

Product Data: Manufacturer’s printed product data sheet for each type of Transmitter/Receiver

specified.

Detail Drawings: Electrical and optical connect drawings. Product mounting template.

Manufacturer’s Installation and Operating Manual: Printed installation and operating

information for each type of Transmitter/Receiver specified.

Test Reports: Manufacturer’s Printed Test Report via a Tektronics VM700A Video Test

Generator verifying product performance meets or exceeds the specified product performance

referenced in Part 2.

Warranty: Manufacturer’s Printed Warranty

DELIVERY, STORAGE AND HANDLING

Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.

Inspect product upon delivery to assure that

specified products have been received.

Store in original packaging in a climate controlled environment. Storage Temperature

not to exceed: -40˚ C to +85˚ C

PROJECT/SITE CONDITIONS

Temperature Requirements: Products shall operate in an environment with an ambient

temperature range of –40˚ C to +74˚ C without

the assistance of fan-forced cooling.

Humidity Requirements: Products shall operate in an environment with relative humidity of 0%

to 95% (non-condensing). If product is installed in condensation conditions, unit shall have conformal coating applied to the printed circuit board.

WARRANTY

A.   Standard International Fiber Systems Comprehensive Lifetime Warranty: IFS

warrants the product to be free of factory defects

under manufacture’s Lifetime Warranty as submitted under article 1.05 (E)

PART 2 - PRODUCTS

MANUFACTURER

Acceptable Manufacturer: International Fiber

Systems, Inc.; 16 Commerce Road, Newtown, CT 06470 USA; Telephone: 203-426-1180; Fax

203-426-3326; Email: sales@ifs.com; Internet:

www.ifs.com

Substitutions: Not Permitted

All fiber optic modules shall be supplied from a single manufacturer.

MANUFACTURED UNITS

Model Number Descriptions: Reference Table A: Product Number Descriptions

Model Compatibility Chart: Reference Table B: Product Compatibility Chart

GENERAL SPECIFICATIONS

A.   The FM Video Transmitter/Receiver and integrated data transceiver system shall be an

IFS VT/ VR9930WDM series. The module shall

be capable of transmitting full color video in real time in NTSC, PAL or SECAM formats.  The module shall support the transmission of simplex or duplex RS-232/422 and 2-wire RS-485 data. The module shall be transparent to data protocols used by various manufacturers, providing for universal compatibility should future system expansion or changes be required. The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation. The module shall transmit the video and data signals using frequency modulation of the optical signal.  The simultaneous video and data transmission shall utilize an integrated WDM for increased stability and reliability of system performance. The module shall provide power, carrier detect, data transmit, data receive and video status indicating LED’s for monitoring proper system operation. The modules shall provide automatic re-settable solid-state current limiters and independent voltage regulators on each module to reduce the chance of a single point failure of the system. The module shall be hot swappable in a rack mount system to reduce complete system shut down during maintenance or repair. The module shall have an MTBF of

>100,000 hours and operate in an environment of

–40˚ C to +74˚ C and relative humidity between 0% to 95% (non-condensing). The module shall

be UL and ULC listed and CE marked. The

circuit board shall be UL 94 flame rated and

meet all PCI standards. All PC boards shall be designated with part number, PC board number and show appropriate revision number. Housing shall be of all metal construction. All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

VIDEO SPECIFICATIONS

Input Video: 1 volt pk-pk (75 ohms)

Bandwidth: 5 Hz – 10 MHz min., @ -3 dB

Differential Gain: < 3 %.

Differential Phase: < 1.3°.

Tilt: <1%

Signal/Noise Ratio: 60dB

DATA SPECIFICATIONS

Data Interface: EIA RS-232, RS-422, RS-485 2-

wire

Data Encoding: Unit shall be transparent to data encoding (i.e. NRZ, NRZI, Manchester, Bi-

phase)

Data Rate: DC-100 kbps (NRZ)

Operation Mode: Simplex or Full Duplex

OPTICAL SPECIFICATIONS

IFS Model Number VT/VR9930WDM

Optical Fiber: 9/125 micron single mode

Number of Fibers Required: 1

Optical Wavelength: 1300nm/1550nm

WDM: Integrated WDM

Optical Emitter Type:	VT 1300nm Laser

VR 1550nm Laser

Transmitter Output Power: 200µw (-7 dB)

Optical Detector Type: VT 1550nm PIN

VR 1300nm PIN

Receiver Sensitivity: 1µw (-30 dB)

Optical Power Budget: 23 dB

Optical Attenuation: No manual adjustments required

STATUS INDICATORS

Power: On/Red – Off/Off

Carrier Detect: Video Carrier Active/Green – No Video Carrier/Off

Data Transmit:  Data Transmit/Green – No

Data/Off

Data Receive: Data Receive/Yellow – No Data/Off

Video In: Video In/Red – No Video/Off

CONNECTORS

Optical: ST

Power: Terminal Block with Screw Clamps or DB-9P

Data:  DB-25S

Video: BNC (Gold Plated Center-PIN)

ELECTRICAL SPECIFICATIONS

Power:	VT: 12VDC VR: 24 VAC CT

Current Protection: Automatic re-settable solid-

state current limiters

Voltage Regulation: Solid-state, Independent on each board

Circuit Board: UL 94 flame rated and meet all PCI standards.

Rack mount Card: Shall be hot-swappable with IFS Model Number R3 (EIA 19” card cage)

MECHANICAL SPECIFICATIONS

Surface Mount Dimensions: 7.1” x 4.9” x 2.0”

(18.00 cm x 12.45 cm x 2.54 cm)

Rack Mount Dimensions: 7.7” x 5.0” x 2.0”

(19.56 cm x 12.70 cm x 5.08 cm)

Number of Rack Slots: 2

Finish: Module shall be constructed of a metal enclosure with a powder coat finish model Number F63B12 with all connections and indicators silk-screened directly on unit. Rack mount units shall be constructed of anodized aluminum.

Weight: <2.0 lbs./1.0kg

ENVIRONMENTAL SPECIFICATIONS

MTBF: >100,000 Hours

Operating Temp: –40˚ C to +74˚ C

Storage Temp: -40˚ C to +85˚ C

Relative Humidity: 0% to 95% (non- condensing). If product is installed under

condensation conditions, unit shall have

conformal coating applied to the printed circuit board. (Add –C to model number for conformal coated printed circuit board)

REGULATORY AGENCIES/APPROVALS AND LISTINGS

Underwriters Laboratory (UL) Listing Number:

I.T.E. 6D16

Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

UL 94-flame rated PCB board: 94VO D.

ACCESSORIES

Card Cage: IFS Model Number R3 (EIA 19” card cage) shall be available to house and power

rack mount modules.

Blank Panels: IFS Model Number R3-BP shall be available to cover unused rack slots.

PART 3 - EXECUTION

EXAMINATION

Inspect modules before installation.

Modules shall be free of any cosmetic defects or damage.

All optical connectors shall be covered with dust

caps and remain on the module until installing cable connectors to module.

Shipping box shall include the module, power supply and operations manual.

PREPARATION

Standalone Module (Surface Mount)

Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved

detail drawings and in compliance with the IFS mounting template and installation manual.

Rack Mount Module (19” Rack)

Shall be installed in the IFS Model Number R3 card cage. Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the IFS installation manual.

Optical Fibers

Caution: NEVER look into the end of an active optical fiber when using laser light

output. Eye damage can occur. Wear eye

protection when cleaving, terminating, and splicing fiber.

The number and type (multimode or single- mode) of optical fiber shall meet the

requirements of the IFS model number in article 2.06 used in the installation.

All optical fiber cables shall be properly installed and terminated with the mating

optical connectors as submitted in article

2.08 (A).

The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.06.

All optical connectors on cable shall be cleaned in compliance to optical connector

manufactures specifications and covered with dust caps until connection to the fiber optic module.

INSTALLATION

A.   General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the IFS installation and operations manual.

TESTING

Testing the Fiber Optic Video Link.

Verify that the coax and optic fibers are properly connected.

Make sure that power is applied to all fiber optic modules, camera, and video monitor or

other equipment used in the system.

The carrier detect indicator LED should be lit confirming a presence of a carrier signal.

Successful video link operation should be

visible at this point as witnessed by a good quality video picture on the monitor.

Testing the Fiber Optic Data Link.

Verify that the data leads and optical fibers are properly connected.

Make sure that power is applied to all fiber optic modules, controllers, and receiver

drivers or other equipment used in the

system.

Successful data link operation should be confirmed at this point by using the

controller to pan, tilt, and zoom the camera

or communicate with other equipment.

CLEANING

Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

At completion of the installation, dispose of all fiber scraps properly.

MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| VT9930WDM SERIES | DESCRIPTION |
| --- | --- |
| VT9930WDM | SM Video / Data – 1300 <> Data – 1550, 1 Fiber |
| VT9930WDM-R3 | SM Video / Data – 1300 <> Data – 1550, 1 Fiber, Rack Mount |

MAX. DISTANCE*

41 Miles (66KM)

41 Miles (66KM)

Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

| VR9930WDM SERIES | DESCRIPTION |
| --- | --- |
| VR9930WDM | SM Data – 1550 <> Video / Data – 1300, 1 Fiber |
| VR9930WDM-R3 | SM Data – 1550 <> Video / Data – 1300, 1 Fiber, Rack Mount |

MAX. DISTANCE*

41 Miles (66KM)

41 Miles (66KM)

Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

Table B: Product Compatibility Chart

TRANSCEIVER	COMPATIBLE TRANSCEIVER

VT9930WDM	VR9930WDM, VR9930WDM-R3

VT9930WDM-R3	VR9930WDM, VR9930WDM-R3

END OF SECTION