DIVISION 27 21 29

IFS FIVE OR EIGHT PORT INDUSTRIAL GIGABIT ETHERNET UNMANAGED SWITCH

GE-DSG & GE-DSGH Series

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- IFS Five or Eight Port Industrial Gigabit Unmanaged Ethernet Switch

1.02 SECTION INCLUDES

- IFS GE-DSG Series Industrial Gigabit Ethernet Switch – Standalone

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide up to 5 or 8 10/100/1000T copper ports.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of ports/operating temperature specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment.

- Storage Temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements:

- IFS GE-DSG-8: Product shall operate in an environment with an ambient temperature range of –10 Degree C to +60 Degree C without the assistance of fan-forced cooling.

- IFS GE-DSGH-5: Product shall operate in an environment with an ambient temperature range of –40 Degree C to +75 Degree C without the assistance of fan-forced cooling.

- IFS GE-DSGH-8: Product shall operate in an environment with an ambient temperature range of –40 Degree C to +75 Degree C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 5% to 90% (non-condensing).

1.08 WARRANTY

- UTCFS Return and Warranty Policy: UTCFS warrants the product to be free of factory defects for a period of 3 years.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand
UTC Fire & Security, Inc. 
8985 Town Center Parkway
Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: presales@interlogix.com

- Substitutions: Not Permitted

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Industrial Gigabit Ethernet switch with 10/100/1000Base-T copper ports system shall be an IFS GE-DSG series model.

- The switch shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.

- The switch features five or eight fixed 10/100/1000T electrical ports.

- The switch shall provide two power, power fault and link speed/active status LED for proper system operation monitoring.

- The unit also provides a contact closure for a power fault alarm.

- The switch shall have redundant power supply connections to minimize single point failure.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3ab

- Data Rate: 10/100/1000 Mbps

- Data Ports: 5 or 8

2.05 STATUS INDICATORS

A. System

| 1. | P1 | Green | Lit: indicate the power 1 has power. |
| --- | --- | --- | --- |
| 2. | P2 | Green | Lit: indicate the power 2 has power. |
| 3. | FAULT | Green | Lit: indicate the either power 1 or power 2 has no power. |

B. 10/100/1000Base-T

| 1. | 1000 | Green | Lit: indicates that the Switch is successfully connecting to the network at 1000Mbps. |
| --- | --- | --- | --- |
|  |  |  | Off: indicates that the Switch is successfully connecting to the network at 10Mbps or 100Mbps, or no link. |
|  |  |  | Blink: indicates that the Switch is actively sending or receiving data over that port. |
| 2. | 100 | Green | Lit: indicates that the Switch is successfully connecting to the network at 100Mbps. |
|  |  |  | Off: indicates that the Switch is successfully connecting to the network at 1000Mbps or no link. |
|  |  |  | Blink: Indicates that the switch is actively sending or receiving data over that port. |

2.06 CONNECTORS

- Power: Terminal Block with Screw Clamps.

- Data: RJ-45

- Contact Closure:  Terminal Block with Screw Clamps

2.07 ELECTRICAL SPECIFICATIONS

- Power:

12VDC to 48VDC @ 1A

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

2.08 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 5.3” x 3.8” x 1.26” (135mm x 97mm x 32mm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat.

- Weight:

- IFS P/N GE-DSG-8 < 1.045lbs / 473g

- IFS P/N GE-DSGH-5 < 1lbs. / 455g

- IFS P/N GE-DSGH-8 < 1.045lbs / 473g

2.9 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temperature:

- IFS P/N GE-DSG-5: –10˚ C to +60˚ C

- IFS P/N GE-DSGH-5: –40˚ C to +75˚ C

- IFS P/N GE-DSGH-8: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 5% to 90% (non-condensing).

2.10 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

2.11 ACCESSORIES

- DIN Rail kit

- Wall mount kit

PART 3 - EXECUTION

3.01 EXAMINATION

- All electronic RJ-45 connectors shall be covered with dust caps and remain on the fixed port until installing cable connectors to it.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- DIN Rail Mount Installation

- Shall be mounted on a properly installed DIN Rail adequate for the size and weight of the module.

- The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

3.03 INSTALLATION

- General: Locate Industrial Gigabit Ethernet modules as indicated on the approved detail drawings and install module in compliance with the IFS User’s manual.

3.04 TESTING

- Testing the 10/100/1000T Gigabit Ethernet Copper Link.

- Verify that the data leads and Gigabit UTP ports are properly connected.

- Make sure that power is applied to all Industrial Gigabit modules or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all UTP cable scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| IFS PART NO. | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| GE-DSG-8 | 8 port electrical 10/100/1000T, -10˚ C to 60˚ C | 300 feet (100M) electrical |
| GE-DSGH-5 | 5 port electrical 10/100/1000T, -40˚ C to 75˚ C | 300 feet (100M) electrical |
| GE-DSGH-8 | 8 port electrical 10/100/1000T, -40˚ C to 75˚ C | 300 feet (100M) electrical |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

Table B: Product Compatibility Chart

| IFS Industrial Gigabit Unmanaged Ethernet Switch | COMPATIBLE Ethernet Equipment |
| --- | --- |
| GE-DSG-8 GE-DSGH-5 GE-DSGH-8 | IEEE 802.3u Fast Ethernet standard for 10/100TX protocol IEEE 802.3ab Gigabit Ethernet standard for 10/100/1000T protocol |

## END OF SECTION