DIVISION 27 21 29

IFS 8-PORT 10/100BASE-TX + 2- GIGABIT TP/SPF with optional PoE
and

IFS 7-PORT 10/100BASE-TX + 3- GIGABIT TP/SPF MANAGED INDUSTRIAL SWITCH

GE-DSH SERIES

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

  - SUMMARY

- IFS 8-PORT 10/100BASE-TX + 2- GIGABIT TP/SPF, with optional PoE, and  IFS 7-PORT 10/100BASE-TX + 3- GIGABIT TP/SPF MANAGED INDUSTRIAL SWITCH

1.02 SECTION INCLUDES

- IFS 8-PORT 10/100BASE-TX + 2- GIGABIT TP/SPF

- IFS 8-PORT 10/100BASE-TX + 2- GIGABIT TP/SPF with PoE

- IFS 7-PORT 10/100BASE-TX + 3- GIGABIT TP/SPF MANAGED INDUSTRIAL SWITCH

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- The IFS Managed Industrial Ethernet Switch provides 8 10/100Mbps Fast Ethernet ports and 2 Gigabit TP/SFP combo interfaces, or 7 10/100Mbps Fast Ethernet ports and 3 Gigabit TP/SFP combo interfaces delivered in a rugged high-strength case.

- The IFS GE-DSH-82-PoE Managed PoE Industrial Switch provides 8 10/100Mbps Fast Ethernet ports and 2 Gigabit TP/SFP combo interfaces with 8 full powered PoE ports (no port sharing) delivered in a rugged high-strength case.

  - The PoE in-line power is compliant with the IEEE 802.3af standard providing 15.4W per port that can power devices at a distance up to 100 meters through the 4-pair Cat 5/5e UTP wire.

  - Full PoE per IEEE802.3af standards (15.4 W) shall be provided to each of the 8 ports with no PoE sharing between ports.

- The Gigabit TP / SFP combo ports can be either 10 / 100 / 1000Mbps on TP ports or 1000Base-SX / LX only through the SFP (Small Form-Factor Pluggable) interface.

- The SFP module shall utilize 1310nm optics capable of bi-directional data transmission of 100Base-FX on multimode or single-mode optical fibers.

- The SFP module shall utilize 850nm optics capable of bi-directional data transmission of 1000Base-SX on two multimode optical fibers.

- The SFP module shall utilize 1310nm optics capable of bi-directional data transmission of 1000Base-LX on two single-mode optical fibers.

- The SFP module shall utilize 1310nm/1490nm or 1310nm/1550nm optics capable of bi-directional data transmission of 1000Base-BX on one single-mode optical fiber.

- The IFS GE-DSH Series is an industrially hardened and fully managed Ethernet Switch specifically designed to operate reliably in electrically harsh and climatically demanding environments.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for the Managed industrial switch.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing).

1.08 WARRANTY

- UTCFS Return and Warranty Policy: UTCFS warrants the product to be free of factory defects for period of 3 years.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand
UTC Fire & Security, Inc. 
8985 Town Center Parkway
Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: presales@interlogix.com

- Substitutions: Not Permitted

- All fiber optic modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Managed Industrial Ethernet Switch transceiver system shall be an IFS GE-DSH Series module.

- The module features seven or eight fixed 10/100TX electrical ports

- The module features two or three fixed 10/100/1000T electrical ports.

- The module shall support the transmission of up to 2 or 3 channels of 100 Mbps over a multimode or single-mode fiber.

- The module shall support the transmission of up to 2 or 3 channels of 1000 Mbps over a multimode or single-mode fiber.

- The module shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.

- The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.

- The module shall provide power, power fault, Ring master, link speed, and fiber port status indicating LED’s for monitoring proper system operation.

- The module shall have redundant power supply connections to minimize single point failure.

- The module shall provide a RS-232 serial connection for local management of the device.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3/3u/3ab/3z

- Data Rate:

  - TP Ports: 10/100/1000 Mbps

  - SFP Ports: 100/1000 Mbps

- Ports: 10

- Operation Mode: Half-duplex or Full-duplex

2.05 OPTICAL SPECIFICATIONS

- IFS Model Number GE-DSH-82

- Optical Interface: 3.3V SFP (Small Form-Factor Pluggable) slot

- Number of SFP Optical ports:2

- Optical Fiber:

- 62.5/125 micron multimode

- 9/125 micron single-mode

- Number of Fibers Required: 1 or 2, vary on SFP module

- Optical Wavelength:

  - 100FX multimode: 1300/1310nm

  - 100FX single-mode: 1310nm

  - 1000SX multimode: 850nm

  - 1000LX singe-mode: 1310nm

- Optical Power Budget: very on SFP module

- Maximum Distance: 74.56 miles (120km)

- IFS Model Number GE-DSH-82-POE

- Optical Interface: 3.3V SFP(Small Form-Factor Pluggable) slot

- Number of SFP Optical ports:2

- Optical Fiber:

- 62.5/125 micron multimode

- 9/125 micron single-mode

- Number of Fibers Required: 1 or 2, vary on SFP module

- Optical Wavelength:

  - 100FX multimode: 1300/1310nm

  - 100FX single-mode: 1310nm

  - 1000SX multimode: 850nm

  - 1000LX singe-mode: 1310nm

- Optical Power Budget: vary on SFP module

- Maximum Distance: 74.56 miles (120km)

- IFS Model Number GE-DSH-73

- Optical Interface: 3.3V SFP(Small Form-Factor Pluggable) slot

- Number of SFP Optical ports:3

- Optical Fiber:

- 62.5/125 micron multimode

- 9/125 micron single-mode

- Number of Fibers Required: 1 or 2, vary on SFP module

- Optical Wavelength:

  - 100FX multimode: 1300/1310nm

  - 100FX single-mode: 1310nm

  - 1000SX multimode: 850nm

  - 1000LX singe-mode: 1310nm

- Optical Power Budget: vary on SFP module

- Maximum Distance: 74.56 miles (120km)

2.06 STATUS INDICATORS

A. System

| 1. | PWR | Green | The switch is on |
| --- | --- | --- | --- |
| 2. | R.M. | Green | The industrial switch is the master of Ring group |
| 3. | PWR1 | Green | Lit: indicate the power 1 has power. |
| 4. | PWR2 | Green | Lit: indicate the power 2 has power. |
| 5. | FAULT | Red | Lit: indicate the either power 1 or power 2 has no power. |

B. 10/100Base-TX

| 1. | 10/100 | Green | Lit: indicates that the Switch is successfully connecting to the network at 100Mbps. |
| --- | --- | --- | --- |
|  |  |  | Off: indicates that the Switch is successfully connecting to the network at 10Mbps. |
|  |  |  | Blinking: Indicates that port is transmitting or receiving packets from the TX device. |
| 2. | Duplex | Amber | Lit: Indicates that port is operating in full-duplex mode. |
|  |  |  | Off: Indicates that port is in half-duplex mode or no device is attached. |

C. 1000Base-T

| 1. |  | LNK/ACT | Green |  | Lit: To indicate the link through that port is successfully established. |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Blink: To indicate that the switch is actively sending or receiving data over that port. |
| 2 | Speed |  |  | Green | Lit: 1000Mbps. Off: 10Mbps or 100Mbps |

D. SFP

| 1. | LNK/ACT | Green | Lit: Indicates that the link through that port is successfully established. |
| --- | --- | --- | --- |
|  |  |  | Blink: Indicates that the switch is actively sending or receiving data over that port. |

E. PoE LED (GE-DSH-82-PoE)

| 1. | PoE In-Use | Green | Lit: Indicates that the port is providing 48VDC in-line power. |
| --- | --- | --- | --- |

2.07 CONNECTORS

- Optical: SFP slot

- Power:  Terminal Block with Screw Clamps.

- Data: RJ-45

- Contact Closure:  Terminal Block with Screw Clamps

- DI/DO: Terminal Block with Screw Clamps (GE-DSH-73 only)

- Console:RJ-45 type RS-232 serial com.

2.08 ELECTRICAL SPECIFICATIONS

- Power:

- IFS P/N: GE-DSH-82 / GE-DSH-73: 12VDC to 48VDC, 1A max.

- IFS P/N: GE-DSH-82-PoE: 48VDC, 4.2A max.

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 2.83” x 4.13” x 5.98” (72 mm x 105 mm x 152 mm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat.

- Weight: <2.31 lbs./1046g

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board.

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE) with following standard:

- EN 55022:2006, Class A

- EN61000-3-2:2006

- EN61000-3-3+A2:2005

- EN 55024+A2:2003

2.12 ACCESSORIES

- DIN Rail kit

- Wall mount kit

PART 3 - EXECUTION

3.01 EXAMINATION

- All electronic RJ-45 connectors shall be covered with dust caps and remain on the fixed port  until installing cable connectors to it

- All optical connectors shall be covered with dust caps and remain on the module until installing cable connectors to module.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- DIN Rail Mount Installation

- Shall be mounted on a properly installed DIN Rail adequate for the size and weight of the module.

- The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type - multimode of optical fiber shall meet the requirements of the IFS model number.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors.

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the IFS User’s manual.

3.04 TESTING

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the 10/100TX PoE Copper output capability of IFS GE-DSH-82-PoE.

- Testing the DC redundant power system is well functioned.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| IFS PART NO. | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| GE-DSH-82 | 8-Port 10/100Mbps + 2-Port Gigabit TP/SFP Combo Managed Industrial Switch (-40~75˚ C) | Varies with SFP module |
| GE-DSH-82-POE | 8-Port 10/100Mbps + 2-Port Gigabit TP/SFP Combo Managed PoE Industrial Switch(-40~75˚ C) | Varies with SFP module |
| GE-DSH-73 | 7-Port 10/100Mbps + 3-Port Gigabit TP/SFP Combo Managed Industrial Switch (-40~75˚ C) | Varies with SFP module |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

Table B: Product Compatibility Chart

| IFS Industrial Fast Ethernet Switch | COMPATIBLE REPEATER / TRANSCEIVER |
| --- | --- |
| GE-DSH-82, GE-DSH-82-PoE, GE-DSH-73 | IEEE 802.3u standard TX and FX base for 10/100TX and 100FX protocol IEEE 802.3ab standard copper base for 1000Base-T protocol IEEE 802.3z standard fiber base for 1000Base-SX/LX |

## END OF SECTION