DIVISION 27 21 29

IFS 4-PORT TO FIBER 
FAST ETHERNET 
SWITCH/MEDIA CONVERTER

MC250-4T/1Fx SERIES

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

  - SUMMARY

- 4-port to Fiber Fast Ethernet Industrial Media Converter (-40~75 Degree C)

1.02 SECTION INCLUDES

- IFS MC250-4T/1FM  4-Port Fast Ethernet to 1-Port MM fiber Industrial Media Converter – 2km (-40~75 Degree C) – Standalone

- IFS MC250-4T/1FS  4-Port Fast Ethernet to 1-Port SM fiber Industrial Media Converter – 15km (-40~75 Degree C) – Standalone

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide up to 4 10/100TX ports and 1 or 2 100FX optical multimode ports.

- The system shall utilize 1310nm optics capable of bi-directional data transmission of 100Mbps on two multimode optical fibers.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of Transmitter/Receiver specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -40˚C to +85˚C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚C to +75˚C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing).

1.08 WARRANTY

- UTCFS Return and Warranty Policy: UTCFS warrants the product to be free of factory defects for period of 3 years.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand

UTC Fire & Security, Inc.
 8985 Town Center Parkway
Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: presales@interlogix.com

- Substitutions: Not Permitted

- All fiber optic modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

2.03 GENERAL SPECIFICATIONS

- The Industrial Fast Ethernet switch with fiber optical transceiver system shall be an MC250-4T/1FM / MC250-4T/1FS module.

- The module shall support the transmission of 1channel of 100 Mbps over a multimode / single mode fiber.

- The module shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.

- The module features four fixed 10/100TX electrical ports and one 100FX optical port.

- The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.

- The module shall provide two power inputs, power fault, link speed, link / act and fiber port status indicating LED’s for monitoring proper system operation.

- The unit shall provide a contact closure for a power fault alarm.

- The module shall have redundant power supply connections to minimize single point failure.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: 10/100 Mbps

- Data Inputs: 4

- Operation Mode: Simplex or Duplex

2.05 OPTICAL SPECIFICATIONS

- IFS Model Number MC250-1T/1FM

- Optical Fiber: 62.5/125 micron multimode

- Number of Optical ports: 1

- Number of Fibers Required: 2

- Optical Wavelength: 1310nm

- Optical Power Budget: 10dB

- Maximum Distance: 1.2 miles (2km)

- IFS Model Number MC250-1T/1FS

- Optical Fiber: 9/125 micron single mode

- Number of Optical ports: 1

- Number of Fibers Required: 2

- Optical Wavelength: 1310nm

- Optical Power Budget: 13dB

- Maximum Distance: 8 miles (15km)

2.06 STATUS INDICATORS

A. System

| 1. | P1 | Green | Lit: indicates that power 1 has power. |
| --- | --- | --- | --- |
| 2. | P2 | Green | Lit: indicates that power 2 has power. |
| 3. | FAULT | Green | Lit: indicates that either power 1 or power 2 has no power. |

B. 10/100Base-TX

| 1. | 10/100 | Green | Lit: indicates that the Switch is successfully connecting to the network at 100Mbps. |
| --- | --- | --- | --- |
|  |  |  | Off: indicates that the Switch is successfully connecting to the network at 10Mbps. |
| 2. | LNK/ACT | Green | Lit: Indicates that the link through that port is successfully established. |
|  |  |  | Blink: Indicates that module is actively sending or receiving data over that port. |

C. 100Base-FX

| 1. | 100 | Green | Lit: indicates that the Switch is successfully connecting to the network at 100Mbps. |
| --- | --- | --- | --- |
| 2. | LNK/ACT | Green | Lit: Indicates that the link through that port is successfully established at 100Mbps. |
|  |  |  | Blink: Indicates that the switch is actively sending or receiving data over that port. |

2.07 CONNECTORS

- Optical: SC

- Power:  Terminal Block with Screw Clamps.

- Data: RJ-45

- Contact Closure:  Terminal Block with Screw Clamps

2.08 ELECTRICAL SPECIFICATIONS

- Power:12VDC to 48VDC @ 1A

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 5.3” x 3.8” x 1.26” (135mm x 97mm x 32mm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat.

- Weight: <0.961 lbs./436g

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board.

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE) with following standard:

- EN 55022:2006, Class A

- EN61000-3-2:2006

- EN61000-3-3+A2:2005

- EN 55024+A2:2003

2.12 ACCESSORIES

- DIN Rail kit

- Wall mount kit

PART 3 - EXECUTION

3.01 EXAMINATION

- All electronic RJ-45 connectors shall be covered with dust caps and remain on the fixed port  until installing cable connectors to it

- All optical connectors shall be covered with dust caps and remain on the interface until installing cable connectors to it.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- DIN Rail Mount Installation

- Shall be mounted on a properly installed DIN Rail adequate for the size and weight of the module.

- The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type - multimode of optical fiber shall meet the requirements of the IFS model number.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors.

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the IFS User’s manual.

3.04 TESTING

- Testing the 10/100TX Fast Ethernet Copper Link.

- Verify that the data leads and UTP ports are properly connected.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| IFS MODEL | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| MC250-4T/1FM | 4 port electrical 10/100TX, MM 1 port 100FX (1310nm), 2 Fibers per port | 328 feet (100M) electrical 1.2 Miles (2KM) optical |
| MC250-4T/1FS | 4 port electrical 10/100TX, SM 1 port 100FX (1310nm), 2 Fibers per port | 328 feet (100M) electrical 8 Miles (15KM) optical |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

## END OF SECTION