DIVISION 27 21 29

IFS 4-Port 10/100TX over Phone Wire / Coax Industrial Media Converter

MC250-4T-1CXT

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- IFS MC250-4T/1CXT 4-Port 10/100TX over Phone Wire / Coax Industrial Ethernet Media Converter

1.02 SECTION INCLUDES

- IFS MC250-4T/1CXT 4-Port 10/100TX over Phone Wire / Coax Industrial Media Converter– Standalone

1.03 REFERENCES

- Federal Communications Commission (FCC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 1 VDSL2 combo port (with RJ-11 port) and 4 10/100Base-TX copper ports.

- The system shall utilize 50 ohm, RG6, RG58A/U, RG58C/U, RG58/U or equivalent coaxial cable for VDSL2 BNC port.

- The system shall utilize EIA568, category 5/5e, 4-pair cables for 10Base-T or 100Base-TX.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of Transmitter/Receiver specified.

- Warranty: Manufacturer’s Printed Warranty.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment.

- Storage Temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Product shall operate in an environment with an ambient temperature range of -40˚C to +75˚C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 5% to 90% (non-condensing).

1.08 WARRANTY

- Standard Interlogix Inc. Comprehensive Warranty: Interlogix warrants the product to be free of factory defects under manufacture’s 3 Years Warranty.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand
UTC Fire & Security, Inc.
8985 Town Center Parkway
Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: presales@interlogix.com

- Substitutions: Not Permitted

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Industrial Ethernet Extender shall be an IFS MC250-4T/1CXT module.

- Ethernet Port:

- The module shall support the Ethernet data IEEE 802.3/802.3u 10/100Base-TX protocol using Auto-negotiating and Auto-MDI/MDI-X features.

- The module features four fixed 10/100TX electrical ports in a compact mini box.

- The module shall support UTP distance up to 100 meters.

- VDSL2 Port:

- The module shall comply with ITU-T G.993.1, G.993.2 VDSL/VDSL2 and SG15Q4 DMT.

- The module shall utilize coaxial cable or RJ-11 telephone wire for the digital subscriber line.

- The module shall equipped with a 4-Position DIP-Switch for selectable Master/ Slave, Fast/Inter leave mode, Asymm / Symm and SNR.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3u

- Data Rate: 10/100 Mbps

- Data Inputs: 4

- Operation Mode: Simplex or Duplex

2.05 VDSL2 SPECIFICATIONS

- IFS Model Number MC250-4T/1CXT.

- Encoding: VDSL-DMT

- Number of VDSL2 port: 1 VDSL2 combo port (with RJ-11 port)

- Maximum Distance (RJ-11): 1.0 miles (1.6km)- Twisted-pair telephone wires (AWG24 or better)

- Maximum Distance (VDSL2): 1.86 miles (3km)- 50 ohm, RG58A/U, RG58C/U, RG58/U or 75 ohm, RG6 BNC cable

2.06 STATUS INDICATORS

A. System

| LED | Color | Function |
| --- | --- | --- |
| P1 | Green | Lit: indicates that the power 1 has power. |
| P2 | Green | Lit: indicates that the power 2 has power. |
| FAULT | Green | Lit: indicates that either power 1 or power 2 do not have power. |

- VDSL

| LED | Color | Function |  |
| --- | --- | --- | --- |
| ACT | Green | Off | Indicates that the VDSL port of Industrial Ethernet Extender is not actively sending or receiving data. |
|  |  | Fast Blink | Indicates that the VDSL port of Industrial Ethernet Extender is actively sending or receiving data. |
| Sync | Green | Lit | Indicates that the VDSL link is established. |
|  |  | Fast Blink | Indicates that the VDSL link is at training status. |
|  |  | Slow Blink | Indicates that the VDSL link is at idle status. |
| Master | Green | Lit | Indicates that the Industrial Ethernet Extender is running at Master mode. |
| Slave | Green | Lit | Indicates that the Industrial Ethernet Extender is running at Slave mode. |

- 10/100Base-TX Port

| LED | Color | Function |  |
| --- | --- | --- | --- |
| LNK/ACT | Green | Lit | Indicates that the port is link up. |
|  |  | Blink | Indicates that the Industrial Ethernet Extender is actively sending or receiving data over that port. |
|  |  | Off | Indicates that the port is link down. |

2.07 CONNECTORS

- Power: Terminal Block with Screw Clamps

- Contact Closure:  Terminal Block with Screw Clamps

- VDSL2 Port: 1 VDSL2 combo port (BNC / RJ-11 connector)

- Ethernet Port: RJ-45

2.08 ELECTRICAL SPECIFICATIONS

- Power:

- 12VDC to 48VDC @ 1A

- 24V AC (AC Range: 18V~30V AC)

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 5.3” x 3.4” x 1.26” (135mm x 87mm x 32mm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat.

- Weight < 0.936lbs / 425g

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: –40˚ C to +75˚ C

- Relative Humidity: 5% to 90% (non-condensing).

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE) with following standard:

- EN 55022:2006, Class A

- EN61000-3-2:2006

- EN61000-3-3+A2:2005

- EN 55024+A2:2003

2.12 ACCESSORIES

- DIN Rail kit

- Wall mount kit

- RJ-11 Telephone line

PART 3 - EXECUTION

3.01 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

3.02 INSTALLATION

- General: Locate Industrial Ethernet Extender module as indicated on the approved detail drawings and install module in compliance with the IFS User’s manual.

- The device is used for Point-to-Point connection only (Master device to Slave device).

- The BNC connector supports 50 ohm cable. Depending on the quality of coaxial cable, the maximum distance of one VDSL segment is 3km with coaxial cable.

- The RJ-11 connector support twisted-pair telephone or ISDN wires (AWG24 or better); the maximum distance of one VDSL segment is 1.6km with RJ-11 telephone wire.

- The distance will change by the quality of coaxial or RJ-11 cables.

- Set the MC250-4T/1CXT to Master mode or Slave mode from the DIP switch at the front panel.

3.03 TESTING

- Testing the 10/100TX Fast Ethernet Copper Link.

- Verify that the data leads and UTP ports are properly connected.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the VDSL2 coaxial cable / RJ-11 telephone wire link.

- Set the one MC250-4T/1CXT to be Master mode and the other MC250-4T/1CXT to be Slave mode.

- Power on the MC250-4T/1CXT by connecting its DC power source.

- Connect coaxial cable between the VDSL BNC ports of the two MC250-4T/1CXT devices.

- VDSL Sync LED will from blinking to illuminate.

- Connect RJ-11 telephone wire between the VDSL RJ-11 ports of the two MC250-4T/1CXT devices.

- VDSL Sync LED will from blinking to illuminate.

3.04 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of the fiber scrap properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| IFS PART NO. | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| MC250-4T/1CXT | 4-Port 10/100TX over Phone Wire / Coax Industrial Ethernet Extender | 300 feet (100M) electrical 1.0 Miles (1.6KM) coaxial cable / RJ-11 telephone wire |

Table B: Product Compatibility Chart

| IFS PART NO. | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| MC250-4T/1CXT | 4-Port 10/100TX over Phone Wire / Coax Industrial Ethernet Extender | 300 feet (100M) electrical 1.0 Miles (1.6KM) coaxial cable / RJ-11 telephone wire |

## END OF SECTION