DIVISION 27 21 29

IFS – 10/100/1000T TO MINI-GBIC SFP INDUSTRIAL MANAGED MEDIA CONVERTER

MC355-1T/1S

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- IFS MC355-1T/1S 1port 10/100/1000Mbps TP to 1 port mini-GBIC slot Industrial Managed Media Converter

1.02 SECTION INCLUDES

- IFS MC355-1T/1S Industrial Managed Media Converter – Standalone

1.03 REFERENCES

- Federal Communications Commission (FCC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 1 10/100/1000T port and 1 1000Base-SX/LX mini-GBIC slot.

- The system shall utilize EIA568, category 5/5e/6, 4-pair cables for 10Base-T or 100Base-TX and 1000Base-T to transfer Ethernet data.

- The system shall utilize 850nm to 1550nm optics capable of data transmission of 1000Mbps on multimode / singlemode optical fibers.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for each type of Transmitter/Receiver specified.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -40˚C to +85˚C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –30˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 5% to 90% (non-condensing).

1.08 WARRANTY

- UTCFS Return and Warranty Policy: UTCFS warrants the product to be free of factory defects for period of 3 years.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand
UTC Fire & Security, Inc.
8985 Town Center Parkway
Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: 	presales@interlogix.com

- Substitutions: Not Permitted

- All fiber optic SFP modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Industrial Managed Media Converter with one 10/100/1000Base-T copper port and one 1000Base-SX/LX mini-GBIC slot system shall be an IFS MC355-1T/1S

- The 1000Base-SX/LX mini-GBIC slot shall support 1000Mbps singlemode / multimode fiber

- The 10/100/1000Base-T port shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.

- The module features one fixed 10/100/1000T electrical port and one 1000SX/LX mini-GBIC optical port.

- The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.

- The module shall provide two powers, power fault, link speed, and fiber port status indicating LED’s for system operation monitoring.

- The unit also provides a contact closure for a power fault alarm.

- The module shall have redundant power supply connections to minimize single point failure.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: 10/100/1000 Mbps

- Data Input: 1

- Operation Mode: Simplex or Duplex

2.05 OPTICAL SPECIFICATIONS

- IFS Model Number MC355-1T/1S

- Optical Fiber:

- 9/125 micron single mode

- 62.5/125 micron multimode

- Number of Optical ports: 1

- Number of Fibers Required: 1 or 2, depend on various SFP module

- Optical Wavelength: depend on various SFP module

- Optical Power Budget: depend on various SFP module

- Maximum Distance: depend on various SFP module

2.06 STATUS INDICATORS

A. System

| 1. | P1 | Green | Lit: indicates that the power 1 has power. |
| --- | --- | --- | --- |
| 2. | P2 | Green | Lit: indicates that the power 2 has power. |
| 3. | FAULT | Green | Lit: indicates that either power 1 or power 2 has no power. |

B. 10/100/1000Base-T

| 1. | 1000 | Green | Lit: indicates that the Switch is successfully connecting to the network at 1000Mbps. |
| --- | --- | --- | --- |
|  |  |  | Off: indicates that the Switch is successfully connecting to the network at 10/100Mbps. |
| 2. | LNK/ACT | Green | Lit: Indicates that the link through that port is successfully established. |
|  |  |  | Blink: Indicates that module is actively sending or receiving data over that port. |

C. 1000Base-SX/LX mini-GBIC port

| 1. | LNK/ACT | Green | Lit: Indicates that the link through that port is successfully established at 1000Mbps. |
| --- | --- | --- | --- |
|  |  |  | Blink: Indicates that the switch is actively sending or receiving data over that port. |

2.07 CONNECTORS

- Optical: SFP Slot / LC interface

- Power:  Terminal Block with Screw Clamps.

- Data: RJ-45

- Contact Closure:  Terminal Block with Screw Clamps

2.08 ELECTRICAL SPECIFICATIONS

- Power:

12VDC to 48VDC @ 1A

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 5.3” x 3.3” x 1.26” (135mm x 85mm x 32mm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat.

- Weight: <0.932 lbs./423g

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –30˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 5% to 90% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board.

  - REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE) with following standard:

- EN 55022:2006, Class A

- EN61000-3-2:2006

- EN61000-3-3+A2:2005

- EN 55024+A2:2003

2.12 ACCESSORIES

- DIN Rail kit

- Wall mount kit

PART 3 - EXECUTION

3.01 EXAMINATION

- All electronic RJ-45 connectors shall be covered with dust caps and remain on the fixed port  until installing cable connectors to it

- All optical connectors shall be covered with dust caps and remain on the interface until installing cable connectors to it.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- DIN Rail Mount Installation

- Shall be mounted on a properly installed DIN Rail adequate for the size and weight of the module.

- The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type - multimode of optical fiber shall meet the requirements of the IFS model number MC355-1T/1S.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors.

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the IFS User’s manual.

3.04 TESTING

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| IFS PART NO. | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| MC355-1T/1S | 10/100/1000-T to mini-GBIC Industrial Managed Media Converter | Depend on various SFP module |

Table B: SFP Transceiver Compatibility Chart

| IFS PART NO. | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| S30-2MLC | SFP-Port 1000Base-SX mini-GBIC module - 220m | 0.14 or 0.34 Miles (220m or 550m) |
| S35-2MLC | SFP-Port 1000Base-SX mini-GBIC module - 220m, Hardened | 0.14 or 0.34 Miles (220m or 550m) |
| S30-2MLC-2 | SFP-Port 1000Base-SX mini-GBIC module – 2km | 1.25 miles (2km) |
| S30-2SLC-10 | SFP-Port 1000Base-LX mini-GBIC module – 10Km | 6.21 Miles (10KM) |
| S35-2SLC-10 | SFP-Port 1000Base-LX mini-GBIC module – 10Km, Hardened | 6.21 Miles (10KM) |
| S30-2SLC-30 | SFP-Port 1000Base-LX mini-GBIC module – 30Km | 18.64 Miles (30KM) |
| S35-2SLC-30 | SFP-Port 1000Base-LX mini-GBIC module – 30Km, Hardened | 18.64 Miles (30KM) |
| S30-2SLC-70 | SFP-Port 1000Base-LX mini-GBIC module – 70Km | 43.49 Miles (70KM) |
| S35-2SLC-70 | SFP-Port 1000Base-LX mini-GBIC module – 70Km, Hardened | 43.49 Miles (70KM) |
| S30-1SLC/A-10 | SFP-Port 1000Base-BX mini-GBIC module A-End (1310/1490nm) – 10Km | 6.21 Miles (10KM) |
| S30-1SLC/B-10 | SFP-Port 1000Base-BX mini-GBIC module B-End (1490/1310 nm) – 10Km | 6.21 Miles (10KM) |
| S30-1SLC/A-20 | SFP-Port 1000Base-BX mini-GBIC module A-End (1310/1490nm) – 20Km | 12.42 Miles (20KM) |
| S30-1SLC/B-20 | SFP-Port 1000Base-BX mini-GBIC module B-End (1490/1310 nm) – 20Km | 12.42 Miles (20KM) |
| S30-1SLC/A-60 | SFP-Port 1000Base-BX mini-GBIC module A-End (1310/1490nm) – 60Km | 37.28 Miles (60KM) |
| S30-1SLC/B-60 | SFP-Port 1000Base-BX mini-GBIC module B-End (1490/1310 nm) – 60Km | 37.28 Miles (60KM) |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

## END OF SECTION