DIVISION 27 21 29

IFS NS2051-4P/1T and  MC251-4P/1S  – 4-PORT FAST ETHERNET/POE-AF INDUSTRIAL UNMANAGED SWITCH/MEDIA CONVERTER

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- 4-Port Fast Ethernet/PoE-AF Industrial Unmanaged Switch/Media Converter (-40~75 Degree C)

1.02 SECTION INCLUDES

- IFS NS2051-4P/1T 5-Port Fast Ethernet Industrial Unmanaged Switch with 4 PoE-AF Ports (-40~75 Degree C) – Standalone

- IFS MC251-4P/1S 4-Port Fast Ethernet/PoE-AF to 1-Port SFP Industrial Media Converter (-40~75 Degree C) – Standalone

1.03 REFERENCES

- Federal Communications Commission (FCC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 1 100Base-FX mini-GBIC slot, or, 1 10/100Base-TX port and 4 10/100Base-TX ports with IEEE 802.3af Power over Ethernet Injector.

- The System shall utilize 1310nm optics capable of bi-directional data transmission of 100Mbps on two multimode or single mode optical fibers. (MC251-4P/1S)

- The system shall utilize EIA568, category 5/5e, 4-pair cables for 10Base-T or 100Base-TX to transfer Ethernet data and 48V DC power simultaneously.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for the PoE Injector.

- Warranty: Manufacturer’s Printed Warranty.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -40˚C to +85˚C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚C to +75˚C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing).

1.08 WARRANTY

- UTCFS Return and Warranty Policy: UTCFS warrants the product to be free of factory defects for period of 3 years.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand
UTC Fire & Security, Inc.
8985 Town Center Parkway
Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: 	presales@interlogix.com

- Substitutions: Not Permitted

- All fiber optic modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The 4/5-Port with 4-Port POE unmanaged Industrial Fast Ethernet switch/media converter shall be NS2051-4P/1T or MC251-4P/1S.

- The switch features 5 10/100TX electrical ports or 4 10/100TX electrical ports with 1 100FX optical SFP slot.

- The switch shall support the Ethernet data IEEE 802.3/802.3u 10/100Base-TX protocol using Auto-negotiating and Auto-MDI/MDI-X features.

- The switch shall support IEEE802.3af Power over Ethernet detection and 48VDC power injection at port#1 to port#4.

- The switch is also equipped with power injectors which transmit DC Voltage to the Cat5/5e cable and transfer data and power simultaneously to remote PD (Powered Device) equipments.

- Switch/media converter shall auto-detect PoE IEEE 802.3af compliant PD equipment and protect devices from being damaged by installation faults.

- The switch/media converter shall support UTP distance up to 100 meters (328 ft).

- The switch shall provide power, fiber port status, copper port status and PoE in-use status indicator LED’s for monitoring proper system operation.

- The module shall inject DC power into the pin of the twisted pair cable (pair 1, 2 and pair 3, 6).

- The switch shall be connected with EIA568A/B Cat 5/5e/6 UTP/STP cable system on its RJ-45 interface ports.

- The switch shall support total distance up to 100 meters (328 ft.) on each PoE port.

- The module shall have redundant power supply connections to minimize single point of failure.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.u

- Data Rate: 10/100 Mbps

- Data Inputs: 2

- Operation Mode: Duplex

2.05 OPTICAL SPECIFICATIONS

- IFS ISW-514PT.

- Optical Fiber: 62.5/125 micron multimode

- Optical Fiber: 9/125 micron single mode

- Number of Optical ports: 1 (MC251-4P/1S only)

- Number of Fibers Required: 2 (MC251-4P/1S only)

- Optical Wavelength: vary on SFP module

- Optical Power Budget: vary on SFP module

- Maximum Distance: vary on SFP module

2.06 STATUS INDICATORS

A. System

| LED | Color | Function |
| --- | --- | --- |
| P1 | Green | Lit: indicates that the power 1 has power. |
| P2 | Green | Lit: indicates that the power 2 has power. |
| FAULT | Green | Lit: indicates that either power 1 or power 2 has no power. |

- 10/100Base-TX Port

| LED | Color | Function |  |
| --- | --- | --- | --- |
| LNK /ACT | Green | Blink | Indicates that the switch is actively sending or receiving data over that port. |
|  |  | Lit | Indicates that the port is link up. |
|  |  | Off | Indicates that the port is link down. |
| PoE in Use (Port 1 to port 4) | Orange | Lit | Indicates that the port is providing 48VDC to remote powered device. |
|  |  | Off | Indicates that the port is not providing 48VDC to remote powered device. |

- 100Base-FX SFP Slot

| LED | Color | Function |  |
| --- | --- | --- | --- |
| LNK /ACT | Green | Blink | Indicates that the switch is actively sending or receiving data over that port. |
|  |  | Lit | Indicates that the port is link up at 100Mbps. |
|  |  | Off | Indicates that the port is link down. |

2.07 CONNECTORS

- Optical: SFP (MC251-4P/1S only)

- Power:  Terminal Block with Screw Clamps.

- Data: RJ-45

- Contact Closure:  Terminal Block with Screw Clamps

2.08 ELECTRICAL SPECIFICATIONS

- Power: 24VDC or 48VDC @ 3.5A

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions (HxDxW): 5.3” x 3.4” x 2.20” (135mm x 87mm x 56mm)

- Finish: Module shall be constructed of a metal enclosure.

- Weight < 1.85lbs / 842g

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board.

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE) with following standard:

- EN 55022:2006, Class A

- EN61000-3-2:2006

- EN61000-3-3+A2:2005

- EN 55024+A2:2003

2.12 ACCESSORIES

- DIN Rail kit

- Wall mount kit

PART 3 - EXECUTION

3.01 EXAMINATION

- All electronic RJ-45 connectors shall be covered with dust caps and remain on the fixed ports until the installation of cables.

- All optical connectors shall be covered with dust caps and remain on the interface until installing cable connectors to it.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- DIN Rail Mount Installation

- Shall be mounted on a properly installed DIN Rail adequate for the size and weight of the module.

- The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type - multimode of optical fiber shall meet the requirements of the IFS model number.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors.

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the IFS User’s manual.

3.04 TESTING

- Testing the 10/100TX Fast Ethernet Copper Link.

- Verify that the data leads and UTP ports are properly connected.

- Make sure that power is applied to the PoE Injector module or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the 10/100TX PoE Copper output capability.

- Make sure that power is applied to the PoE switch.

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| IFS MODELS | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| NS2051-4P/1T | 5-Port 10/100Base-TX with 4-Port PoE Wide Temperature Industrial Fast Ethernet Switch | 328 feet (100M) electrical |
| MC251-4P/1S | 4-Port 10/100Base-TX + 1-Port 100Base-FX SFP with 4-Port PoE Wide Temperature Industrial Fast Ethernet Switch | 328 feet (100M) electrical Depend on various SFP module |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

Table B: Product Compatibility Chart  (only MC251-4P/1S)

| IFS SFP Transceiver | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| SFP100FX1310TSC2KM | SFP-Port 100Base-FX Transceiver (1310nm) -2km | 1.24 Miles (2KM) |
| SFP100FX1310TSC20KM | SFP-Port 100Base-FX Transceiver (1310nm) -20km | 12.42 Miles (20KM) |
| S20-2MLC-2 | SFP-Port 100Base-FX Transceiver (1310nm) -2km | 1.24 Miles (2KM) |
| S25-2MLC-2 | SFP-Port 100Base-FX Transceiver (1310nm) -2km – Hardened | 1.24 Miles (2KM) |
| S20-2SLC-20 | SFP-Port 100Base-LX Transceiver (1310nm) -20km | 12.42 Miles (20KM) |
| S25-2SLC-20 | SFP-Port 100Base-LX Transceiver (1310nm) -20km - Hardened | 12.42 Miles (20KM) |
| S20-1SLC/A-20 | SFP-Port 100Base-BX A-end (1310/1550nm) -20km | 12.42 Miles (20KM) |
| S20-1SLC/B-20 | SFP-Port 100Base-BX B-end (1550/1310nm) -20km | 12.42 Miles (20KM) |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

## END OF SECTION