DIVISION 27 21 29

IFS NS3550-24T/4S 24-PORT 10/100/1000-T INDUSTRIAL MANAGED SWITCH WITH 4 SHARED MINI-GBIC SLOTS

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- IFS NS3550-24T/4S Twenty-four 10/100/1000Mbps TP Port with four shared mini-GBIC slot Industrial Managed Switch

1.02 SECTION INCLUDES

- IFS NS3550-24T/4S: 24-Port Gigabit with 4 shared mini-GBIC slots Industrial Managed Switch– Standalone

1.03 REFERENCES

- Underwriters Laboratory (UL)

- Underwriters Laboratory Canada (ULC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provides 24 10/100/1000T ports and 4 shared 1000Base-SX/LX mini-GBIC slots.

- The system shall utilize EIA568, category 5/5e/6, 4-pair cables for 10Base-T or 100Base-TX and 1000Base-T to transfer Ethernet data.

- The system shall utilize 850nm to 1550nm optics capable with data transmission of 1000Mbps on multimode / single mode optical fibers.

- The Gigabit TP / SFP combo ports can either be 1000Base-T for 10 / 100 / 1000Mbps or optical 1000Base-SX / LX through SFP (Small Form-Factor Pluggable) interface.

- The SFP module shall utilize 850nm optics capable of bi-directional data transmission of 1000Base-SX on two multimode optical fibers.

- The SFP module shall utilize 1310nm optics capable of bi-directional data transmission of 1000Base-LX on two single-mode optical fibers.

- The SFP module shall utilize 1310nm/1490nm or 1310nm/1550nm optics capable of bi-directional data transmission of 1000Base-BX on one single-mode optical fiber.

- The SFP module shall utilize 1310nm optics capable of bi-directional data transmission of 100Base-FX on multimode or single-mode optical fibers.

1.05 SUBMITTALS

- Manufacturer’s Quick Installation Guide and Operating Manual: Printed installation guide and operating information for the Industrial Managed Switch.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment. Storage Temperature not to exceed: -40˚C to +85˚C

- Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.

- Inspect product upon delivery to assure that specified products have been received.

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing).

1.08 WARRANTY

- UTCFS Return and Warranty Policy: UTCFS warrants the product to be free of factory defects for period of 3 years.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand
UTC Fire & Security, Inc.
8985 Town Center Parkway
Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: 	presales@interlogix.com

- Substitutions: Not Permitted

- All fiber optic modules shall be supplied from a single manufacturer.

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Managed Ethernet switch shall be the IFS NS3550-24T/4S model.

- The Industrial Gigabit Ethernet switch shall be equipped with twenty-four 10/100/1000Base-T copper ports with four shared 1000Base-SX/LX mini-GBIC slots.

- The switch shall comply with IEEE 802.3, 802.3u, 802.3ab and 802.3z Ethernet standards.

- The 10/100/1000Base-T port shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.

- The 1000Base-SX/LX mini-GBIC slot support 1000Mbps single mode / multimode fiber.

- The switch shall provide a RS-232 serial connection for local management of the device.

- The switch shall be a 1U (one U, 1.75 inches) 19-inch rack mountable equipment that can be installed in standard cabinet or 19-inch rack.

- The switch shall be connected with EIA568A/B Cat 5/5e/6 UTP/STP cable system on its RJ-45 interface ports.

- The module shall require no in-field electrical or optical adjustments or in-line attenuators to simplify installation.

- The module shall provide two power, power fault, link / act status, and fiber port status indicating LED’s for monitoring proper system operation.

- The unit shall provide a contact closure for a power fault alarm.

- The module shall have redundant power supply connections to minimize single point failure.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3/3u/3ab/3z

- Data Rate: 10/100/1000 Mbps

- Data Input: 24

- Operation Mode: Simplex or Duplex

2.05 OPTICAL SPECIFICATIONS

- IFS NS3550-24T/4S:

- Optical Interface: 3.3V SFP (Small Form-Factor Pluggable) slot

- Number of SFP Optical ports:4

- Optical Fiber:

- 62.5/125 micron multimode

- 9/125 micron single-mode

- Number of Fibers Required: 1 or 2, vary on SFP module

- Optical Wavelength:

  - 100FX multimode: 1300/1310nm

  - 100FX single-mode: 1310nm

  - 1000SX multimode: 850nm

  - 1000LX singe-mode: 1310nm

- Optical Power Budget: varies with SFP module

- Maximum Distance: 43.49 miles (70km)

2.06 STATUS INDICATORS

- System

| 1. | DC1 | Green | Indicates that the DC 1 has power. |
| --- | --- | --- | --- |
| 2. | DC2 | Green | Indicates that the DC 2 has power. |
| 3. 4. | FAULT PWR | Amber Green | Indicates that the either DC 1 or DC or both 2 has no power. Indicates that the switch has power. |

B. 10/100/1000Base-T

| 1. | 1000 LNK/ ACT | Green | Illuminates to indicate the link through that port is successfully established with speed 1000Mbps |
| --- | --- | --- | --- |
|  |  |  | Blinks to indicate that the switch is actively sending or receiving data over that port. |
| 2 | 10/100 LNK/ ACT | Green | Illuminates to indicate the link through that port is successfully established with speed 10Mbps or 100Mbps. Blinks to indicate that the switch is actively sending or receiving data over that port. |

C. 1000Base-SX/LX mini-GBIC port

| 1. | 1000 LNK/ ACT | Green | Illuminates to indicate that the link through that port is successfully established with speed 1000Mbps |
| --- | --- | --- | --- |
|  |  |  | Off: indicate that Switch is not connecting to the network at 1000Mbps. |
|  |  |  | Blinks to indicate that the switch is actively sending or receiving data over that port. |

2.07 CONNECTORS

- Optical: SFP Slot / LC interface.

- Terminal Block with Screw Clamps.

- Data: RJ-45.

- Console: DB9 Type RS-232 serial com.

2.08 ELECTRICAL SPECIFICATIONS

- Power Characteristics of NS3550-24T/4S:

- Power: 36VDC to 72VDC @ 1A

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 17” x 7.8” x 1.75” (440mm x 200mm x 44.5mm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat.

- Weight: < 5.9 lbs./2.69kg

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: > 50,000 Hours

- Operating Temp: -40˚ C to +75˚ C

- Storage Temp: -40˚ C to +80˚ C

- Relative Humidity: 10% to 90% (non-condensing).

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Underwriters Laboratory (UL) Listing Number: I.T.E. 6D16

- Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE) with following standard:

- EN 55022:2006, Class A

- EN61000-3-2:2006

- EN61000-3-3+A2:2005

- EN 55024+A2:2003

2.12 ACCESSORIES

- Rubber feet

- Rack-mount brackets

- RS-232 DB9 male console cable

PART 3 - EXECUTION

3.01 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module.

- The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- Rack Mount Module (19” Rack)

- The unit is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the rack mount unit. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the user’s manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type - multimode of optical fiber shall meet the requirements of the IFS model number.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors.

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.02 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the IFS User’s manual.

3.03 TESTING

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the 10/100/1000T Fast Ethernet and Gigabit Copper Link.

- Verify that the data leads and UTP ports are properly connected.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

3.04 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| IFS MODEL | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| NS3550-24T/4S | 24-Port 10/100/1000Mbps with 4 Shared SFP Industrial Managed Switch | Vary on SFP module |

Table B: Product Compatibility Chart

| IFS SFP Transceiver | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| S30-RJ | SFP-Port SFP100-T mini-GBIC module – 100m | 0.06 Miles (100m) |
| S30-2MLC | SFP-Port 1000Base-SX mini-GBIC module - 220m – Industrial (-40 ~75 °C) | 0.14 or 0.34 Miles (220m or 550m) |
| S30-2MLC-2 | SFP-Port 1000Base-SX mini-GBIC module – 2km | 1.25 miles (2km) |
| S35-2MLC | SFP-Port 1000Base-SX mini-GBIC module - 220m | 0.14 or 0.34 Miles (220m or 550m) |
| S30-2SLC-10 | SFP-Port 1000Base-LX mini-GBIC module – 10Km | 6.21 Miles (10KM) |
| S30-2SLC-30 | SFP-Port 1000Base-LX mini-GBIC module – 30Km | 18.64 Miles (30KM) |
| S30-2SLC-70 | SFP-Port 1000Base-LX mini-GBIC module – 70Km | 43.49 Miles (70KM) |
| S35-2SLC-10 | SFP-Port 1000Base-LX mini-GBIC module – 10Km – Industrial (-40 ~75 °C) | 6.21 Miles (10KM) |
| S35-2SLC-30 | SFP-Port 1000Base-LX mini-GBIC module – 30Km – Industrial (-40 ~75 °C) | 18.64 Miles (30KM) |
| S35-2SLC-70 | SFP-Port 1000Base-LX mini-GBIC module – 70Km – Industrial (-40 ~75 °C) | 43.49 Miles (70KM) |
| S30-1SLC/A-10 | SFP-Port 1000Base-BX mini-GBIC module A-End (1310/1490nm) – 10Km | 6.21 Miles (10KM) |
| S30-1SLC/B-10 | SFP-Port 1000Base-BX mini-GBIC module B-End (1490/1310 nm) – 10Km | 6.21 Miles (10KM) |
| S30-1SLC/A-20 | SFP-Port 1000Base-BX mini-GBIC module A-End (1310/1490nm) – 20Km | 12.42 Miles (20KM) |
| S30-1SLC/B-20 | SFP-Port 1000Base-BX mini-GBIC module B-End (1490/1310 nm) – 20Km | 12.42 Miles (20KM) |
| S30-1SLC/A-60 | SFP-Port 1000Base-BX mini-GBIC module A-End (1310/1490nm) – 60Km | 37.28 Miles (60KM) |
| S30-1SLC/B-60 | SFP-Port 1000Base-BX mini-GBIC module B-End (1490/1310 nm) – 60Km | 37.28 Miles (60KM) |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

## END OF SECTION