DIVISION 27 21 29

IFS -  IEEE 802.3AF POE EXTENDER

POE201-EX

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- IFS POE201-EX IEEE 802.3af PoE EXTENDER

1.02 SECTION INCLUDES

- IFS POE201-EX IEEE 802.3af PoE EXTENDER – Standalone

1.03 REFERENCES

- Federal Communications Commission (FCC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provides 2 RJ-45 ports in a compact mini enclosure. One of the ports (IN) functions as "PoE (Data and Power) input" and the other port on the other side functions (OUT) as "PoE (Data and Power) output". The "PoE OUT" port also injects the power by transmitting DC Voltage to the Cat5e/6 cable and transfer data and power simultaneously to the PD.

- The system shall utilize EIA568, category 5/5e, 4-pair cables for 10Base-T or 100Base-TX to transmit Ethernet data and power simultaneously into the PoE Extender.

- The POE201-EX PoE Extender is easy to install by simple plug and play operation. It is used between a Power Source Equipment (PSE) and the Powered Device (PD) by extending the distances.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for the PoE Extender.

- Warranty: Manufacturer’s Printed Warranty.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment.

- Storage Temperature not to exceed: -40˚C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Product shall operate in an environment with an ambient temperature range of -5 Degree C to +50 Degree C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing).

1.08 WARRANTY

- UTCFS Return and Warranty Policy: UTCFS warrants the product to be free of factory defects for period of 3 years.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand
UTC Fire & Security, Inc.
8985 Town Center Parkway
Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: presales@interlogix.com

- Substitutions: Not Permitted

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Power over Ethernet Extender shall be an IFS POE201-EX module.

- The module shall comply with IEEE 802.3af Power over Ethernet.

- The module shall support the Ethernet data IEEE 802.3/802.3u 10/100Base-TX protocol using Auto-negotiating and Auto-MDI/MDI-X features.

- The module features two fixed 10/100TX electrical ports in a compact mini box of PoE Extender.

- The port printed with “IN” functions as " IEEE 802.3af PoE “Data + DC” Input".

- The port on the other side and printed with “OUT” functions as " IEEE 802.3af PoE “Data + DC” output".

- The module shall forward both Ethernet data and PoE power to remote devices

- The module shall support daisy-chain installation of multiple units.

- The module shall auto-detect and protect PoE equipment from being damaged by incorrect installation

- The module shall require no external power cable for installation

- Compact size, Wall-mountable / DIN-Rail design

- The module shall receive power from either data (UTP PIN 1,2,3,6) or spare pairs (UTP PIN 4,5,7,8) by IEEE802.3af standard

- The module shall support total distance up to 100 meters.

- The module shall provide PoE IN, LNK/ACT, and PoE Out LED indicators for proper monitoring of operation.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.u

- Data Rate: 10/100 Mbps

- Data Inputs: 2

2.05 STATUS INDICATORS

A. LED Definition:

| LED | Color | Function |
| --- | --- | --- |
| PoE IN | Green | Indicates that the port is providing 48VDC in-line power. |
| LNK/ACT | Green | Indicates that the port link is active. Blink: indicates that the switch is actively sending or receiving data over IN port. |
| PoE OUT | Green | Indicates that the port is providing 48VDC in-line power. |

2.06 CONNECTORS

- LAN IN Port: RJ-45

- LAN OUTPort: RJ-45

2.07 ELECTRICAL SPECIFICATIONS

- Power Requirement

- IEEE 802.3af compliant with voltage within 44V-56V DC

- Power Consumption

1. 2Watts (maximum)

2.08 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions (WxDxH): 3.54” x 2.75” x 0.98” inches (95 x 70 x 25mm)

- Finish: Module shall be constructed of a metal enclosure.

- Weight < 0.47lbs / 215g

2.9 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >50,000 Hours

- Operating Temp: -5˚ C to +50˚ C

- Storage Temp: -10˚ C to +85˚ C

- Relative Humidity: 0% to 95% (non-condensing).

2.10 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE) with following standard:

- EN 55022:2006, Class A

- EN61000-3-2:2006

- EN61000-3-3+A2:2005

- EN 55024+A2:2003

2.11 ACCESSORIES

- User’s Manual x1

PART 3 - EXECUTION

3.01 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

3.02 INSTALLATION

- General: Locate PoE Extender module as indicated on the approved detail drawings and install module in compliance with the IFS User’s manual.

- Connect POE201-EX to the Power Source Equipment (PSE)

Step 1: 	Connect a standard Cat5e/6 UTP cable from Power Source Equipment (PSE), such as PoE Switch, PoE Injector hub and single port PoE injector, to the “IN” port of POE201-EX.

Step 2: 	The PSE delivers both Ethernet Data and PoE power over UTP cable to the POE201-EX. “PoE IN” LED will illuminate to indicate this operation.

- Connect POE201-EX to the Powered Device (PD)

Step 3: 	Connect the additional CAT5e/6 cable that will be used to connect to the remote Powered Device (PD) to the “OUT” port of POE201-EX.

Step 4: 	The "OUT" port also injects power by transmitting DC Voltage to the Cat5e/6 cable and transfer data and power simultaneously to the PD.

Step 5: 	Once POE201-EX detects the existence of an IEEE 802.3af PD, the “PoE OUT” LED indicator will illuminate to indicate that it is providing power.

- Multiple PoE Extender Installation

Step 1: 	Connect the additional CAT5e/6 cable from the “OUT” port of the first POE201-EX, the other end of the UTP cable be used to connect to the “IN” port of the next POE201-EX.

Step 2: 	The “PoE OUT” LED indicator of the first POE201-EX will be ON to show it is providing power to next PoE Extender.

Step 3: 	The “PoE IN” LED on the next POE201-EX will steady on.

Step 4: 	Connect the additional CAT5e/6 cable to the remote PoE powered device to the “OUT” port of next or third POE201-EX.

3.03 TESTING

- Testing the 10/100TX Fast Ethernet Copper Link.

- Verify that the data leads and UTP ports are properly connected.

- Make sure that power is applied to the PoE Extender module or other equipment used in the system.

- Successful data link operation should be established at this point by the communication with connected equipment.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all UTP cable scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| IFS PART NO. | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| POE201-EX | IEEE 802.3AF POE EXTENDER | 100M at each side |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

Table B: Product Compatibility Chart

| IFS PART NO. | COMPATIBLE Ethernet Equipment |
| --- | --- |
| POE201-EX | IEEE 802.3u Fast Ethernet standard for 10/100TX protocol IEEE 802.3af Power over Ethernet |

## END OF SECTION