DIVISION 27 21 29

IFS – IEEE 802.3AT GIGABIT POE INJECTOR

POE302-MS

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- IFS POE302-MS IEEE 802.3at Gigabit PoE Injector (Mid-Span)

1.02 SECTION INCLUDES

- POE302-MS IEEE 802.3at High Power Over Gigabit Ethernet Mid-Span Injector – Standalone

1.03 REFERENCES

- Federal Communications Commission (FCC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provides 1 10/100/1000Base-T copper port with IEEE 802.3at Power over Ethernet injector capability.

- The system shall utilize EIA568, category 5/5e/6, 4-pair cables for 10Base-T, 100Base-TX or 1000Base-T to transfer data and 56V DC power simultaneously.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for the PoE Injector.

- Warranty: Manufacturer’s Printed Warranty.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment.

- Storage Temperature not to exceed: -10˚ C to +70˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Product shall operate in an environment with an ambient temperature range of 0°C to +50°C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 5% to 90% (non-condensing).

1.08 WARRANTY

- UTCFS Return and Warranty Policy: UTCFS warrants the product to be free of factory defects for period of 3 years.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand
UTC Fire & Security, Inc.
8985 Town Center Parkway
Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: presales@interlogix.com

- Substitutions: Not Permitted

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Power over Ethernet Injector shall be an IFS POE302-MS module.

- The module shall comply with IEEE 802.3at Power over Ethernet standard.

- The module shall support the Ethernet data IEEE 802.3/802.3u/802.3ab 10/100/1000Base-T protocol using Auto-negotiating and Auto-MDI/MDI-X features.

- The module features two fixed 10/100/1000T electrical ports in a compact mini box.

- The port printed with “Ethernet” functions as "Data input".

- The other port on the other side and printed with “Ethernet + DC” functions as "PoE (Data and Power) output".

- The module also injects power by transmitting DC Voltage to the Cat5/5e/6 cable and transfer data and power simultaneously between the PSE and PD.

- The module shall Auto-detect PoE IEEE 802.3at equipment and shall protect devices from being damaged by incorrect installation.

- The module shall support total distance up to 100 meters.

- The module shall provide power and PoE in-use status LED indicators for the proper monitoring of operation.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3

- Data Rate: 10/100 /1000 Mbps

- Data Inputs: 2

2.05 STATUS INDICATORS

A. LED Definition:

| LED | Color | Function |
| --- | --- | --- |
| Power | Yellow | Indicates that the POE302-MS has power. |
| PoE Ready / in-use | Green | Indicates that the port is providing 56VDC in-line power. |

2.06 CONNECTORS

- Power: DC plug female

- Data:

- Ethernet Port: RJ-45

- Ethernet + DC Port: RJ-45

2.07 ELECTRICAL SPECIFICATIONS

- Power Adapter:

- Input Voltage Range: 100~240VAC

- Output Voltage: 56VDC @ 0.53A

- The PoE Injector:

- Input Voltage: 56VDC

2.08 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions (WxDxH): 3.54” x 2.75” x 0.98” (95 x 70 x 25mm)

- Finish: Module shall be constructed of a metal enclosure.

- Weight < 0.18lbs / 83g

2.9 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >50,000 Hours

- Operating Temp: 0˚ C to +50˚ C

- Storage Temp: -10˚ C to +70˚ C

- Relative Humidity: 5% to 90% (non-condensing).

2.10 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE) with following standard:

- EN 55022:2006, Class B

- EN61000-3-2:2006

- EN61000-3-3+A2:2005

- EN 55024+A2:2003

2.11 ACCESSORIES

- AC-to-DC 56V Power Adapter x1 (not included)

- Power cord x 1 (UK ,AU, AG, IR and SW only)

PART 3 - EXECUTION

3.01 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

3.02 INSTALLATION

- General: Locate PoE Injector module as indicated on the approved detail drawings and install module in compliance with the IFS User’s manual.

3.03 TESTING

- Testing the 10/100/1000T Gigabit Ethernet Copper Link.

- Verify that the data leads and UTP ports are properly connected.

- Make sure that power is applied to the PoE Injector module or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the 10/100/1000T PoE Copper output capability.

3.04 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all UTP cable scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| IFS PART NO. | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| POE302-MS | IEEE 802.3AT GIGABIT MID-SPAN POE+ INJECTOR | 300 feet (100m) electrical |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

Table B: Product Compatibility Chart

| IFS PART NO. | COMPATIBLE Ethernet Equipment |
| --- | --- |
| POE302-MS | IEEE 802.3/802.3u/802.3ab Ethernet standard for 10/100/1000T protocol IEEE 802.3at High Power over Ethernet PD |

## END OF SECTION