DIVISION 27 21 29

POC2502-8CXP-2T-2S–

8-port Power over Coax Switch

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- 8-port Power over Coax Switch

1.02 SECTION INCLUDES

- POC2502-8CXP-2T-2S 8-port Ethernet over Coax Receiver with PoC/PoE+ – Standalone

1.03 REFERENCES

- Federal Communications Commission (FCC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 8 BNC ports, 2 10/100/1000BASE-T copper ports and 2 100/1000BASE-SX/LX SFP slots.

- The system shall utilize RG6/U, RG59/U BNC port to transfer Ethernet data and power simultaneously

- The system shall utilize EIA568, category 5/5e, 4-pair cables for 10BASE-T/100BASE-TX/1000BASE-T to transfer Ethernet data.

- The system shall utilize 850nm to 1550nm optics capable of data transmission of 100/1000Mbps on multimode / single mode optical fibers.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for the PoC Switch.

- Warranty: Manufacturer’s Printed Warranty.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment.

- Storage Temperature not to exceed: -10˚ C to +70˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Product shall operate in an environment with an ambient temperature range of 0˚C to +50˚C with the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 5% to 95% (non-condensing).

1.08 WARRANTY

- Standard UTC Fire & Security Inc. Comprehensive Warranty: UTC Fire & Security warrants the product to be free of factory defects under manufacture’s 3 Years Warranty.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand

UTC Fire & Security, Inc.

3211 Progress Drive,

Lincolnton, NC 28092

- Phone 1-855-286-8889

- Email: presales@interlogix.com

- Substitutions: Not Permitted

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The management PoC Switch shall be a POC2502-8CXP-2T-2S

- Ethernet Port:

- The switch features two fixed 10/100/1000BASE-T electrical ports

- The switch features two 1000BASE-SX/LX optical SFP slots.

- The switch shall be connected with EIA568A/B Cat 5/5e/6 UTP/STP cable system for its RJ45 interface ports.

- The switch shall support UTP distance up to 100 meters.

- Coaxial Port:

- The switch shall comply with IEEE 1901 standard.

- The switch shall utilize coaxial cable for the digital subscriber line.

- The switch shall equipped Wavelet-OFDM schemes.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE802.3/3u/3ab/3z

- Data Rate:

- GE1 to GE2 10/100/1000Mbps

- GE3 to GE4 SFP: 100/1000 Mbps

- Data Inputs: GE1 to GE4

- Operation Mode: Simplex or Duplex

2.05 POC SPECIFICATIONS

- UTC Fire & Security Model Number

- POC2502-8CXP-2T-2S.

- Number of POC port: 8 (BNC connector)

- Cabling:

• Coaxial cable: 75 ohm

• RG-6/U cable, less than 12Ω/1,000ft.

• RG-59/U cable, less than 30Ω/1,000ft.

- Maximum Distance:

• Max. 1000m with PoE output (3,280ft.)

• Max. 1,200m with data output only (3,937ft.)

2.06 STATUS INDICATORS

- System (POC)

| LED | Color | Function |
| --- | --- | --- |
| PWR | Green | Lights to indicate the power is on. |
| SYS | Green | Lights to indicate the system is working. |
|  |  | Off to indicate the system is booting. |

- System Alert

| LED | Color | Function |
| --- | --- | --- |
| FAN1 | Red | Lights to indicate that the FAN1 is down. |
| FAN2 | Red | Lights to indicate that the FAN2 is down. |
| FAN3 | Red | Lights to indicate that the FAN3 is down. |
| PWR | Red | Lights to indicate that the PoE Power is down. |

- BNC Port with PoE (FE1 to FE8)

| LED | Color | Function |
| --- | --- | --- |
| LNK | Green | Lights: to indicate the link through that port is successfully established |
| PoC | Amber | Lights: to indicate the port is providing 54VDC in-line power |

- 10/100/1000BASE-T Port (GE1 to GE2)

| LED | Color | Function |
| --- | --- | --- |
| LNK/ ACT | Green | Lights to indicate the link through that port is successfully established. |
|  |  | Blinks to indicate that the switch is actively sending or receiving data over that port. |
| 1000 | Amber | Lights to indicate that the port is operating at 1000Mbps. |
|  |  | Off: if LNK/ACT LED is light, it indicates the port is operating at 10/100Mbps. If LNK/ACT LED is off, it indicates the port is link down |

- 1000BASE-SX/LX SFP Port (GE3 to GE4)

| LED | Color | Function |
| --- | --- | --- |
| LNK/ ACT | Green | Lights to indicate the link through that port is successfully established. |
|  |  | Blinks to indicate that the switch is actively sending or receiving data over that port. |
| 1000 | Amber | Lights to indicate that the port is operating at 1000Mbps. |
|  |  | Off: if LNK/ACT LED is light, it indicates the port is operating at 100Mbps. If LNK/ACT LED is off, it indicates the port is link down |

2.07 CONNECTORS

- BNC Port: 8 BNC connector

- Ethernet Port: 2 Gigabit RJ45 interfaces

- Fiber-optical Port: 2 SFP mini-GBIC slots

- Console Port: 1 RJ45 RS232 port

2.08 ELECTRICAL SPECIFICATIONS

- Power Characteristics of POC2502-8CXP-2T-2S:

- Voltage Input:100~240V AC / 50-60Hz

- Current: 4A max.

- Power Consumption: Maximum 320Watts with PoC full load

- PoC Output Power of POC2502-8CXP-2T-2S:

- Total PoC output budget: 240Watts

- Per PoC output: 36Watts max.

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 17.3” x 11.8” x 1.75” (440mm x 300mm x 44.5mm)

- Finish: Module shall be constructed of a metal enclosure.

- Weight < 9.42lbs / 4282g

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: > 50,000 Hours

- Operating Temp: 0˚ C to +50˚ C

- Storage Temp: –10˚ C to +75˚ C

- Relative Humidity: 5% to 95% (non-condensing).

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE)

2.12 ACCESSORIES

- AC Power cord

- RJ45 to DB9 RS232 cable

- Rubber feet

- Rack-mount kit

- SFP dust cap

- BNC dust cap

- Warning sticker

# PART 3 - EXECUTION

3.01 PREPARATION

- Standalone (Surface Mount)

- Shall be placed on a properly prepared surface adequate for the size and weight of module.

- The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- Rack Mount (19” Rack)

The unit is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the rack mount unit. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the user’s manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number of optical fiber SFP slot shall meet the requirements of the UTC Fire & Security model number.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors.

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budge.

3.02 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the UTC Fire & Security User’s manual.

- The device is used for Point-to-Point or Point-to-Multi-Point connection when POC2502-8CXP-2T-2S connects to POC252-1CX-1P.

- The BNC connector supports 75 ohm cable. Depending on the quality of coaxial cable, the maximum distance is 1km with coaxial cable.

- The distance will change by the quality of coaxial cables.

3.03 TESTING

- Testing the 10/100/1000T Gigabit Ethernet Copper Link.

- Verify that the data LEDs and UTP ports are properly connected.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the 100/1000X SFP Link

- Verify that the data LEDs and SFP ports are properly connected.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the coaxial cable link.

- Power on the POC2502-8CXP-2T-2S by connecting AC power source

- Connect coaxial cable between the BNC ports of the POC2502-8CXP-2T-2S and POC252-1CX-1P devices.

- Login to WEB UI and enable System PoE Admin mode from PoE Configuration WEB page.

- PWR and LNK LEDs will illuminate.

- Connect RJ45 wire from PoE OUT port of POC252-1CX-1P to a PoE device.

- PoE IN-Use and LNK/ACT LEDs of POC252-1CX-1P will illuminate.

- Connect a PC to POC2502-8CXP-2T-2S.

- Access the PoE device from the PC.

3.04 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of the BNC cover properly.

MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| Model Name | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| POC2502-8CXP-2T-2S | 8-port Power over Coax Switch | Max. 1,000m with PoE output (3,280ft.) Max. 1,200m with data output only (3,937ft.) |

*Note: The distance will change by the quality of coaxial cables.

Table B: Product Compatibility Chart

| Model Name | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| POC252-1CX-1P | 1-Port Power over Coax 30W Ethernet Extender | Max. 1,000m with PoE output (3,280ft.) Max. 1,200m with data output only (3,937ft.) |

*Note: The distance will change by the quality of coaxial cables.

## END OF SECTION