DIVISION 27 21 29

POC252-1CX-1P, 1-Port Ethernet over Coax Extender Long Reach with PoE-AT

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- 1-Port Power over Coax 30W Ethernet Extender

1.02 SECTION INCLUDES

- POC252-1CX-1P 1-Port Coaxial to 1-Port Fast Ethernet with POE-AT Extender – Standalone

1.03 REFERENCES

- Federal Communications Commission (FCC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 1 BNC and 1 10/100Base-TX copper port with IEEE 802.3at/af Power over Ethernet Injector.

- The system shall utilize RG6/U, RG59/U BNC port.

- The system shall utilize EIA568, category 5/5e, 4-pair cables for 10Base-T or 100Base-TX to transfer Ethernet data and power simultaneously.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for the PoE Injector.

- Warranty: Manufacturer’s Printed Warranty.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment.

- Storage Temperature not to exceed: -40˚ C to +75˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Product shall operate in an environment with an ambient temperature range of -10˚C to +60˚C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 5% to 95% (non-condensing).

1.08 WARRANTY

- Standard UTC Fire & Security Inc. Comprehensive Warranty: UTC Fire & Security warrants the product to be free of factory defects under manufacture’s 3 Years Warranty.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand

UTC Fire & Security, Inc.

8985 Town Center Parkway

Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: presales@interlogix.com

- Substitutions: Not Permitted

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Industrial Ethernet Extender shall be a POC252-1CX-1P module.

- Ethernet Port:

- The module features one fixed 10/100BASE-TX electrical ports in a compact mini box.

- The module shall support the Ethernet data IEEE 802.3/802.3u 10/100Base-TX protocol using Auto-negotiating and Auto-MDI MDI-X features.

- The module shall comply with IEEE 802.3at/af Power over Ethernet PSE (Power Source Equipment).

- The module shall support UTP distance up to 100 meters.

- Coaxial Port:

- The module shall comply with IEEE 1901 standard.

- The module shall utilize coaxial cable for the digital subscriber line.

- The module shall equipped Wavelet-OFDM schemes.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE 802.3u

- Data Rate: 10/100 Mbps

- Data Inputs: 1

- Operation Mode: Simplex or Duplex

2.05 POC SPECIFICATIONS

- UTC Fire & Security Model Number             POC252-1CX-1P.

- Number of POC port: 1 (BNC connector)

- Cabling:

• Coaxial cable: 75 ohm
• RG-6/U cable, less than 12Ω/1,000ft.
• RG-59/U cable, less than 30Ω/1,000ft.

- Maximum Distance:

• Max. 1000m with PoE output (3,280ft.)

• Max. 1,200m without PoE output (3,937ft.)

2.06 STATUS INDICATORS

A. System (POC)

| LED | Color | Function |
| --- | --- | --- |
| PWR | Green | Light: indicates the power is on. |
| LNK | Green | Light: indicates that the coaxial link is established. |
|  |  | Off: indicates that the coaxial link is down. |

- 10/100Base-TX Port with PoE

| LED | Color | Function |
| --- | --- | --- |
| PoE In-Use | Amber | Light: indicates the RJ45 Port is providing PoE power |
| LNK/ ACT | Green | Blink: indicates the extender is actively sending or receiving data over that port. |

2.07 CONNECTORS

- BNC Port: 1 BNC connector

- Ethernet Port: RJ-45

2.08 ELECTRICAL SPECIFICATIONS

- Power: 48 to 56VDC

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 3.7” x 2.76” x 1.02” (94mm x 70mm x 26mm)

- Finish: Module shall be constructed of a metal enclosure.

- Weight < 0.83lbs / 375g

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –10˚ C to +60˚ C

- Storage Temp: –40˚ C to +75˚ C

- Relative Humidity: 5% to 90% (non-condensing).

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE)

2.12 ACCESSORIES

- DIN Rail kit (optional)

- Wall mount kit

PART 3 - EXECUTION

3.01 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

3.02 INSTALLATION

- General: Locate Industrial Ethernet Extender module as indicated on the approved detail drawings and install module in compliance with the UTC Fire & Security User’s manual.

- The device is used for Point-to-Point connection only if POC-252-1CXP-1T connects to a PoE+ injector (Master device to Slave device).

- The device is used for Point-to-Multi-point connection if POC-252-1CXP-1T connects to 56V DC power adaptor (Master device to Slave device).

- The BNC connector supports 75 ohm cable. Depending on the quality of coaxial cable, the maximum distance is 1.2km with coaxial cable.

- The distance will change by the quality of coaxial cables.

3.03 TESTING

- Testing the 10/100TX Fast Ethernet Copper Link.

- Verify that the data leads and UTP ports are properly connected.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the 10/100TX PoE Copper output capability.

- Testing the coaxial cable link.

- Power on the POC252-1CXP-1T by connecting 56V DC power source or connecting to a POE+ injector.

- Connect coaxial cable between the BNC ports of the POC252-1CXP-1T and POC252-1CX-1P devices.

- PWR and LNK LEDs will from blinking to illuminate.

- Connect RJ45 wire from PoE OUT port of POC252-1CX-1P to a PoE device.

- PoE IN-Use and LNK/ACT LEDs will illuminate.

- Connect a PC to POC252-1CXP-1T.

- Access the PoE device from the PC.

3.04 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of the BNC cover properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| Model Name | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| POC252-1CX-1P | 1-Port Power over Coax 30W Ethernet Extender | Max. 1,000m with PoE output (3,280ft.) Max. 1,200m without PoE output (3,937ft.) |

Table B: Product Compatibility Chart

| Model Name | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| POC252-1CXP-1T | 1-Port Power over Coax 30W Ethernet Transmitter | Max. 1,000m with PoE output (3,280ft.) Max. 1,200m without PoE output (3,937ft.) |
| POC2502-8CXP-2T-2S | 8-port Power over Coax Switch | Max. 1,000m with PoE output (3,280ft.) Max. 1,200m without PoE output (3,937ft.) |
| POC2502-16CXP-2T-2S | 16-port Power over Coax Switch | Max. 1,000m with PoE output (3,280ft.) Max. 1,200m without PoE output (3,937ft.) |

## END OF SECTION