DIVISION 27 21 29

IFS 16-Port Gigabit PoE+ Industrial Managed Switch

NS3552-16P-2T-2S

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- Sixteen 10/100/1000Mbps TP Port with PoE AT plus two RJ45 ports + two mini-GBIC slot Industrial Gigabit Managed Switch

1.02 SECTION INCLUDES

- IFS NS3552-16P-2T-2S 16-Port Gigabit Ethernet PoE+ plus 2 RJ45 + 2 SFP Ports Industrial Managed Switch – Standalone

1.03 REFERENCES

- Federal Communications Commission (FCC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 16 10/100/1000 Base-T copper ports with IEEE 802.3at Power over Ethernet Injector and  2 100/1000 Mbps SFP slots

- The system shall utilize EIA568, category 5/5e/6, 4-pair cables for 10Base-T or 100Base-TX and 1000 Base-T to transfer Ethernet data and 48 to 56 VDC power simultaneously.

- The system shall utilize 850 nm to 1550 nm optics capable of data transmission of 100/1000 Mbps on multimode / single mode optical fibers.

- The SFP ports can be optical 1000Base-SX / LX or 100Base-FX through SFP (Small Form-Factor Pluggable) interface.

- The SFP module shall utilize 850 nm optics capable of bi-directional data transmission of 1000 Base-SX on two multimode optical fibers.

- The SFP module shall utilize 1310 nm optics capable of bi-directional data transmission of 1000 Base-LX on two single-mode optical fibers.

- The SFP module shall utilize 1310 nm/1490 nm or 1310 nm/1550 nm optics capable of bi-directional data transmission of 1000 Base-BX on one single-mode optical fiber.

- The SFP module shall utilize 1310 nm optics capable of bi-directional data transmission of 100 Base-FX on multimode or single-mode optical fibers.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for the Managed Ethernet Switch.

- Warranty: Manufacturer’s Printed Warranty.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment.

- Storage Temperature not to exceed: -40˚ C to +85˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +75˚ C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing).

1.08 WARRANTY

- Standard UTC Fire & Security Inc. Comprehensive Warranty: UTC Fire & Security warrants the product to be free of factory defects under manufacture’s 3 Years Warranty.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand

UTC Fire & Security, Inc.

8985 Town Center Parkway

Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: presales@interlogix.com

- Substitutions: Not Permitted

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Industrial Gigabit Managed Switch shall be an NS3552-16P-2T-2S model.

- The Industrial Gigabit Managed Switch with sixteen 10/100/1000 Base-T copper port plus two RJ45 10/100/1000 Base-t and two 100/1000 Base-X SFP slot system.

- The 10/100/1000 Base-T port shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.

- The 100/1000 Base-X SFP slot support single mode / multimode fiber

- The module shall provide two powers, power fault, Ring and RO, fiber port speed and link / act status, TP port link / act and PoE status indicating LED’s for monitoring proper system operation.

- The unit supports 8 VLAN interfaces, 32 routing entries.

- The unit supports IPv4 and IPv6 software static IP routing between VLAN interfaces.

- The unit also provides a contact closure for a power fault alarm.

- The module shall have redundant power supply connections to minimize single point failure.

- The Fast/Gigabit Ethernet SFP module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.

- The module shall support UTP distance up to 100 meters

- The switch shall be connected with EIA568A/B Cat 5/5e/6 UTP/STP cable system for its RJ45 interface ports.

- The NS3552-16P-2T-2S shall comply with IEEE 802.3at/802.3af Power over Ethernet:

- The NS3552-16P-2T-2S shall support IEEE 802.3at Power over Ethernet detection and 56 VDC power injection maximum ability at port1 to port16.

- The NS3552-16P-2T-2S is also the power injectors which transmit DC Voltage to the Cat5/5e/6 cable and transfer data and power simultaneously to remote PD (Powered Device) equipments.

- The NS3552-16P-2T-2S shall Auto-detect of PoE IEEE802.3at/802.3af equipment; protect devices from being damaged by incorrect installation.

- The NS3552-16P-2T-2S shall support total distance up to 100 meters on PoE ports.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE 802.3/3u/3ab/3z

- Data Rate:

- Port1 to Port18: 10/100/1000 Mbps

- Port19 to Port20 SFP: 100/1000 Mbps

- Data Inputs: 20

- Operation Mode: Simplex or Duplex

2.05 OPTICAL SPECIFICATIONS

- UTC Fire & Security Model Number NS3552-16P-2T-2S

- Optical Fiber:

- 9/125 micron single mode

- 62.5/125 micron multimode

- Number of Optical ports: 2

- Number of Fibers Required: 1 or 2, depend on various SFP module

- Optical Wavelength: depend on various SFP module

- Optical Power Budget: depend on various SFP module

- Maximum Distance: depend on various SFP module

2.06 STATUS INDICATORS

- System

| 1. | P1 | Green | Lit: indicate the power 1 has power. |
| --- | --- | --- | --- |
| 2. | P2 | Green | Lit: indicate the power 2 has power. |
| 3. | FAUL T | Green | Lit: indicate the either power 1 or power 2 has no power. |
| 4. | RING | Green | Lit: indicate that the ERPS Ring has been created successfully. |
| 5. | R.O. | Green | Lit: indicate that Switch has been enabled Ring Owner. |

B. 100/1000X SFP Interfaces

| 1. | LNK/ ACT | Green | Lit: indicate the link through that port is successfully established at 100Mbps or 1000Mbps. Blink: indicate that the switch is actively sending or receiving data over that port. |
| --- | --- | --- | --- |
| 2. | 1000 | Orange | Lit: indicate that the port is successfully established at 1000Mbps. Off: indicate that the port is successfully established at 100Mbps. |

C. 10/100/1000 Base-T Interfaces

| 1. | 10/100/1000 LNK/ ACT | Green | indicate that the port is successfully connecting to the network at 10/100/1000Mbps. Blink: indicate that the switch is actively sending or receiving data over that port. |
| --- | --- | --- | --- |
| 2. | PoE In-Use | Orange | indicate that the port is providing 56V DC in-line power. Off: indicate the connected device is not a PoE Powered Device (PD) |

2.07 CONNECTORS

- Optical: SFP Slot / LC interface

- Power:  Terminal Block with Screw Clamps.

- Data: RJ45

- Console: RJ45-to-DB9 RS-232

- Contact Closure:  Terminal Block with Screw Clamps

2.08 ELECTRICAL SPECIFICATIONS

- Power Characteristics of NS3552-16P-2T-2S:

- Power:

48 VDC @ 7 A

- Current Protection: Automatic re-settable solid-state current limiters

- Voltage Regulation: Solid-state, Independent on each board

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 5.9” x 4.2” x 3.3” (152 mm x 107 mm x 84 mm)

- Finish: Module shall be constructed of a metal enclosure with a powder coat.

- Weight:  3.37 lbs./ 1533 g

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >100,000 Hours

- Operating Temp: –40˚ C to +75˚ C

- Storage Temp: -40˚ C to +85˚ C

- Relative Humidity: 0 % to 95 % (non-condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board.

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE) with following standard:

- EN 55022:2006, Class A

- EN61000-3-2:2006

- EN61000-3-3+A2:2005

- EN 55024+A2:2003

2.12 ACCESSORIES

- RJ45 to RS232 Console Cable

- DIN Rail kit

- Wall mount kit

- Dust Cap

PART 3 – EXECUTION

3.01 EXAMINATION

- All electronic RJ45 connectors shall be covered with dust caps and remain on the fixed port  until installing cable connectors to it

- All optical connectors shall be covered with dust caps and remain on the interface until installing cable connectors to it.

3.02 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- DIN Rail Mount Installation

- Shall be mounted on a properly installed DIN Rail adequate for the size and weight of the module.

- The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

- Optical Fibers

- Caution: NEVER look into the end of an active optical fiber when using laser light output. Eye damage can occur. Wear eye protection when cleaving, terminating, and splicing fiber.

- The number and type - multimode of optical fiber shall meet the requirements of the UTC Fire & Security model number.

- All optical fiber cables shall be properly installed and terminated with the mating optical connectors.

- The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3 dB of optical safety margin does not exceed the optical power budget.

- All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

3.03 INSTALLATION

- General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the UTC Fire & Security User’s manual.

3.04 TESTING

- Testing the Fiber Optic Ethernet Link.

- Verify that the data leads and optical fibers are properly connected.

- Make sure that power is applied to all fiber optic modules, controllers, and receiver drivers or other equipment used in the system.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the 10/100/1000 Base-T Gigabit Ethernet and Gigabit Copper Link.

- Verify that the data leads and UTP ports are properly connected.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the 10/100/1000 Base-T PoE Copper output capability.

3.05 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

- At completion of the installation, dispose of all UTP cable scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| IFS PART NO. | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| NS3552-16P-2T-2S | 16-Port Gigabit PoE+ Industrial Managed Switch | Copper port is 100 meters SFP slot depends on various SFP module |

Table B: Product Compatibility Chart

| SFP Transceiver | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| MULTI-MODE |  |  |
| S30-2MLC | SFP-Port 1000 Base-SX Mini-GBIC Module - 2 Fiber – 550 m - Multi-Mode – 850 nm (0~50℃) - Based on 50/125 µm OM2 Fiber | 550 m |
| S30-2MLC-2 | SFP-Port 1000 Base-SX2 Mini-GBIC Module - 2 Fiber – 2 Km - Multi-Mode – 1310 nm (0~50℃) - Based on 50/125 µm OM4 Laser Optimise | 2 Km |
| SINGLE MODE |  |  |
| S30-2SLC-10 | SFP-Port 1000 Base-LX10 Mini-GBIC Module - 2 Fiber – 10 Km - Single-Mode – 1310 nm (0~50℃) | 10 Km |
| S30-2SLC-30 | SFP-Port 1000 Base-LHX Mini-GBIC Module - 2 Fiber – 30 Km - Single-Mode – 1310 nm (0~50℃) | 30 Km |
| S30-2SLC-70 | SFP-Port 1000 Base-ZX Mini-GBIC Module - 2 Fiber – 70 Km - Single-Mode – 1550 nm (0~50℃) | 70 Km |
| S30-1SLC/A-10 | SFP-Port 1000 Base-BX10 Mini-GBIC Module - 1 Fiber – 10 Km - Single-Mode - Tx 1310 nm - Rx 1490 nm (0~50℃) | 10 Km |
| S30-1SLC/B-10 | SFP-Port 1000 Base-BX10 Mini-GBIC Module - 1 Fiber – 10 Km - Single-Mode - Tx 1490 nm - Rx 1310 nm(0~50 ℃) | 10 Km |
| S30-1SLC/A-20 | SFP-Port 1000 Base-BX20 Mini-GBIC Module - 1 Fiber – 20 Km - Single-Mode - Tx 1310 nm - Rx 1490 nm (0~50℃) | 20 Km |
| S30-1SLC/B-20 | SFP-Port 1000 Base-BX20 Mini-GBIC Module - 1 Fiber – 20 Km - Single-Mode - Tx 1490 nm - Rx 1310 nm (0~50℃) | 20 Km |
| S30-1SLC/A-60 | SFP-Port 1000Base-BX60 Mini-GBIC Module - 1 Fiber - 60Km - Single-Mode - Tx 1310nm - Rx 1490nm (0~50℃) | 60 Km |
| S30-1SLC/B-60 | SFP-Port 1000 Base-BX60 Mini-GBIC Module - 1 Fiber – 60 Km - Single-Mode - Tx 1490 nm - Rx 1310 nm (0~50℃) | 60 Km |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

## END OF SECTION