DIVISION 27 21 29

POE303-MS – PoE-Ultra Gigabit Ethernet

Injector

ENGINEERING SPECIFICATIONS

# PART 1 - GENERAL

1.01 SUMMARY

- 1-Port Power over Ethernet 60W Injector

1.02 SECTION INCLUDES

- POE303-MS 1-Port Gigabit Ethernet to 1-Port Gigabit Ethernet with POE-AT 30W plus 30W injector – Standalone

1.03 REFERENCES

- Federal Communications Commission (FCC)

- European Union Compliance (CE)

1.04 SYSTEM DESCRIPTION

- Performance Requirements: Provide 1 Ethernet with Power over Ethernet Injector and 1 10/100/1000BASE-T copper port with IEEE 802.3at/af PoE PD.

- The system shall utilize EIA568, category 5/5e, 4-pair cables for 10BASE-T, 100BASE-TX or 1000BASE-T to transfer Ethernet data and power simultaneously.

1.05 SUBMITTALS

- Manufacturer’s Installation and Operating Manual: Printed installation and operating information for the Power over Ethernet Injector.

- Warranty: Manufacturer’s Printed Warranty.

1.06 DELIVERY, STORAGE AND HANDLING

- Store in original packaging in a climate controlled environment.

- Storage Temperature not to exceed: -10˚ C to +70˚ C

1.07 PROJECT/SITE CONDITIONS

- Temperature Requirements: Product shall operate in an environment with an ambient temperature range of 0˚C to +50˚C without the assistance of fan-forced cooling.

- Humidity Requirements: Products shall operate in an environment with relative humidity of 5% to 95% (non-condensing).

1.08 WARRANTY

- Standard UTC Fire & Security Inc. Comprehensive Warranty: UTC Fire & Security warrants the product to be free of factory defects under manufacture’s 3 Years Warranty.

# PART 2 - PRODUCTS

2.01 MANUFACTURER

- Acceptable Manufacturer:

- IFS Brand

UTC Fire & Security, Inc.

8985 Town Center Parkway

Bradenton, FL 34202-5129

- Phone 1-855-286-8889

- Email: presales@interlogix.com

- Substitutions: Not Permitted

2.02 MANUFACTURED UNITS

- Model Number Descriptions: Reference Table A: Product Number Descriptions

- Model Compatibility Chart: Reference Table B: Product Compatibility Chart

2.03 GENERAL SPECIFICATIONS

- The Industrial Ethernet Extender shall be a POE303-MS module.

- Ethernet Port:

- The module features one fixed 10/100/1000BASE-T electrical ports in a compact mini box.

- The module shall support the Ethernet data IEEE 802.3/802.3u/802.3z 10/100/1000BASE-T.

- The module shall comply with IEEE 802.3at End-span and Mid-span Power over Ethernet PD (Power Device).

- The module shall support UTP distance up to 100 meters.

2.04 DATA SPECIFICATIONS

- Data Interface: Ethernet IEEE 802.3z

- Data Rate: 10/100/1000 Mbps

- Data Inputs: 1

2.05 PoE SPECIFICATIONS

- UTC Fire & Security Model Number             POE303-MS.

- Number of PoE port: 1 (RJ45 connector)

- Maximum Distance:

• Max. 100m with PoE output (328ft.)

2.06 STATUS INDICATORS

A. System

| LED | Color | Function |
| --- | --- | --- |
| PWR | Green | Light: indicates the power is on. |
| 802.3at End-span | Green | Light:On indicates that the ultra PoE injector is working on End-Span mode and offers up to 30 watts power. |
|  |  | Off: indicates that the End-span mode is not activate. |
| 802.3at Mid-span | Green | Light: On indicates that the ultra PoE injector is working on Mid-Span mode and offers up to 30 watts power. |
|  |  | Off: indicates that the Mid-span mode is not activate. |

2.07 CONNECTORS

- Ethernet Port: RJ45

- PoE Port: RJ45

2.08 ELECTRICAL SPECIFICATIONS

- Power Characteristics of POE303-MS:

- Voltage Input:56VDC

- Current: 1.16A max.

- Power Consumption: Maximum 63Watts with PoE full load

- PoE Output Power of POE303-MS:

- PoE output budget: 60Watts

- IEEE 802.3af class 3 (15.4W): Max. 1 ports

- IEEE 802.3at class 4 End-span (30W): Max. 1 ports

- IEEE 802.3at class 4 Mid-span (30W): Max. 1 ports

2.09 MECHANICAL SPECIFICATIONS

- Surface Mount Dimensions: 3.7” x 2.76” x 1.03” (94mm x 70.3mm x 26.2mm)

- Finish: Module shall be constructed of a metal enclosure.

- Weight < 0.52lbs / 237g

2.10 ENVIRONMENTAL SPECIFICATIONS

- MTBF: >50,000 Hours

- Operating Temp: 0˚ C to +50˚ C

- Storage Temp: –10˚ C to +70˚ C

- Relative Humidity: 5% to 90% (non-condensing).

2.11 REGULATORY AGENCIES/APPROVALS AND LISTINGS

- Federal Communications Commission (FCC) Part 15, Class A

- European Union Compliance (CE)

PART 3 - EXECUTION

3.01 PREPARATION

- Standalone Module (Surface Mount)

- Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the installation manual.

3.02 INSTALLATION

- General: Locate Industrial Ethernet Extender module as indicated on the approved detail drawings and install module in compliance with the UTC Fire & Security User’s manual.

- The device is used for Point-to-Point connection only if POE303-MS connects to a PoE+ device.

- The device supports 100 meters cable length, but because it is not an extender device, so the distance calculation should be from the device of connected to POE303-MS data input port to PoE device.

3.03 TESTING

- Testing the 10/100/1000T Gigabit Ethernet Copper Link.

- Verify that the data leads and UTP ports are properly connected.

- Successful data link operation should be confirmed at this point by communicating with other equipment.

- Testing the 10/100/1000T PoE Copper output capability.

- Testing the copper cable link.

- Power on the POE303-MS by connecting 56VDC power adaptor.

- Connect RJ45 cable between the PoE ports of the POE303-MS and End-span or mid-span PoE device

- PWR and 802.3at End-span/Mid-span LED will light up.

- Connect RJ45 cable between the PoE ports of the POE303-MS and POE-303-EX-4P

- PWR and 802.3at End-span and Mid-span LED will light up both.

- Connect a PC to POE303-MS and make sure RJ45 cable wire length from PC to PoE device has not over 100 meters.

- Access the PoE device from the PC.

3.04 CLEANING

- Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

Caution: Do Not Plug any PSE into the Output of the POE303-MS injector. It will cause damage to the unit.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| Model Name | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| POE303-MS | PoE-Ultra Gigabit Ethernet Injector | Max. 100m between Ethernet port and Ethernet + DC port. |

Table B: Product Compatibility Chart

| Model Name | DESCRIPTION | MAX. DISTANCE* |
| --- | --- | --- |
| POE-303-EX-4P | PoE-Ultra to Gigabit Ethernet 4-Port PoE+ Extender | Max. 100m with PoE input (328ft.) Max. 100m with PoE output (328ft.) |

## END OF SECTION