# DIVISION 28 23 23 VT/VR72430-R3 SERIES – FIBER OPTIC

**TRANSMITTER AND RECEIVER**

**ENGINEERING SPECIFICATIONS**

**PART 1 - GENERAL**

**1.01** SUMMARY

A. Fiber Optic Digital 24 Channel Video Multiplexing System

**1.02** SECTION INCLUDES

A. VT/VR72430-R3 Digital 24 Channel Video Multiplexing System - Rack Mount

* 1. REFERENCES
1. Underwriters Laboratory (UL)
2. Underwriters Laboratory Canada (ULC)
3. European Union Compliance (CE)
	1. SYSTEM DESCRIPTION
4. Performance Requirements: Provide a Digital 24 Channel Video Multiplexing System.
	1. The system shall utilize 1510/1530/1550nm

optics capable of digitally encoding and decoding 24 channels of video on one single mode optical fiber. (VT/VR72430-R3)

* 1. SUBMITTALS
1. Product Data: Manufacturer’s printed product data sheet for each type of Transmitter/Receiver specified.
2. Detail Drawings: Electrical and optical connect drawings. Product mounting template.
3. Manufacturer’s Installation and Operating

Manual: Printed installation and operating information for each type of Transmitter/Receiver specified.

1. Test Reports: Manufacturer’s Printed Test Report via a Tektronics VM700A Video Test

Generator verifying product performance meets

or exceeds the specified product performance referenced in Part 2.

1. Warranty: Manufacturer’s Printed Warranty
	1. DELIVERY, STORAGE AND HANDLING
2. Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.
3. Inspect product upon delivery to assure that specified products have been received.
4. Store in original packaging in a climate controlled environment. Storage Temperature

not to exceed: -40˚ C to +85˚ C

* 1. PROJECT/SITE CONDITIONS
1. Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +74˚ C without the assistance of fan-forced cooling.
2. Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, unit shall have conformal coating applied to the printed circuit board.
	1. WARRANTY

A. Standard International Fiber Systems Comprehensive Lifetime Warranty: IFS warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (E)

# PART 2 - PRODUCTS

* 1. MANUFACTURER
1. Acceptable Manufacturer: International Fiber Systems, Inc.; 16 Commerce Road, Newtown, CT 06470 USA; Telephone: 203-426-1180; Fax

203-426-3326; Email: sales@ifs.com; Internet:

[www.ifs.com](http://www.ifs.com/)

1. Substitutions: Not Permitted
2. All fiber optic modules shall be supplied from a single manufacturer.
	1. MANUFACTURED UNITS
3. Model Number Descriptions: Reference Table A: Product Number Descriptions
4. Model Compatibility Chart: Reference Table B:

Product Compatibility Chart

* 1. GENERAL SPECIFICATIONS

A. The Digital 24-channel video encoding and decoding system shall be an IFS VT/VR72430-R3 series. The rack mount unit shall be capable of digitally encoding and decoding 24 channels of full color video in real time in NTSC, PAL or SECAM formats. The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation. The module shall transmit the video using state – of – the – art digital encoding and decoding of the optical signal. The module shall provide power, local video presence, remote video presence, and automatic gain control (AGC) status indicating LED’s for monitoring proper system operation. The modules shall provide automatic re- settable solid-state current limiters and independent voltage regulators on each module to reduce the chance of a single point failure of the system. The module shall be hot swappable in a rack mount system to reduce complete system shut down during maintenance or repair. The module shall have an MTBF of >100,000 hours and operate in an environment of –40˚ C to +74˚ C and relative humidity between 0% to 95% (non-condensing). The module shall be UL and ULC listed and CE marked. The circuit board shall be UL 94 flame rated and meet all PCI standards. All PC boards shall be designated with part number, PC board number and show appropriate revision number. Housing shall be of all metal construction. All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

* 1. VIDEO SPECIFICATIONS
1. Input Video: 1 volt pk-pk (75 ohms)
2. Bandwidth: 5 Hz – 6.5 MHz
3. Differential Gain: < 2 %
4. Differential Phase: < 0.7 °
5. Tilt: <1%

**F.** Signal/Noise Ratio: 60 dB @ maximum optical loss budget

* 1. OPTICAL SPECIFICATIONS
1. IFS Model Number VT/VR72430-R3
	1. Optical Fiber: 9/125 micron single mode
	2. Number of Fibers Required: 1
	3. Optical Wavelength: 1510/1530/1550nm
	4. Optical Power Budget: 10 dB
	5. STATUS INDICATORS
2. Power: On/Red – Off/Off
3. Local Video Presence: Local Video Presence/Green – No Local Video Present/Red
4. Remote Video Presence: Remote Video Presence/Green – No Remote Video Present/Red
5. Optical Carrier Detect: Optical lock/Green, No lock/Red.
	1. CONNECTORS
6. Optical: ST, SC and FC optional
7. Power: From R3 rack 110/230VAC
8. Video: BNC (Gold Plated Center-PIN)
	1. ELECTRICAL SPECIFICATIONS
9. Current Protection: Automatic re-settable solid- state current limiters
10. Voltage Regulation: Solid-state, Independent on

each board

1. Circuit Board: UL 94 flame rated and meets all PCI standards.
2. Rack mount Card: Shall be hot-swappable with

IFS Model Number R3 (EIA 19” card cage)

* 1. MECHANICAL SPECIFICATIONS
1. Rack Mount Dimensions: 19” x 7.0” x 5.3” (48.3 cm x 17.80 cm x 13.3 cm)
2. Number of Rack Slots: 10
3. Rack mount units shall be constructed of anodized aluminum.
4. Weight: <12.0 lbs./5.4kg
	1. ENVIRONMENTAL SPECIFICATIONS
5. MTBF: >100,000 Hours
6. Operating Temp: –40˚ C to +74˚ C
7. Storage Temp: -40˚ C to +85˚ C
8. Relative Humidity: 0% to 95% (non- condensing). If product is installed under

condensation conditions, unit shall have conformal coating applied to the printed circuit

board. (Add –C to model number for conformal coated printed circuit board)

* 1. REGULATORY AGENCIES/APPROVALS AND LISTINGS
1. Underwriters Laboratory (UL) Listing Number:

I.T.E. 6D16

1. Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16
2. UL 94-flame rated PCB board: 94VO

D.

* 1. ACCESSORIES
1. Card Cage: IFS Model Number R3 (EIA 19” card cage) shall be available to house and power rack mount modules.
2. Blank Panels: IFS Model Number R3-BP shall be available to cover unused rack slots.

# PART 3 - EXECUTION

* 1. EXAMINATION
1. Inspect modules before installation.
2. Modules shall be free of any cosmetic defects or damage.
3. All optical connectors shall be covered with dust

caps and remain on the module until installing cable connectors to module.

1. Shipping box shall include the module, power supply and operations manual.
	1. PREPARATION
2. Rack Mount Module (19” Rack)
	1. Shall be installed in the IFS Model Number R3 card cage. Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the IFS installation manual.
3. Optical Fibers
	1. Caution: NEVER look into the end of an active optical fiber when using laser light

output. Eye damage can occur. Wear eye

protection when cleaving, terminating, and splicing fiber.

* 1. The number and type (multimode or single- mode) of optical fiber shall meet the

requirements of the IFS model number in article 2.05 used in the installation.

* 1. All optical fiber cables shall be properly installed and terminated with the mating

optical connectors as submitted in article

2.07 (A).

* 1. The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.05.
	2. All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.
	3. INSTALLATION

A. General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the IFS installation and operations manual.

* 1. TESTING
1. Testing the Fiber Optic Video Link.
	1. Verify that the coax and optic fibers are properly connected.
	2. Make sure that power is applied to all fiber optic modules, camera, and video monitor or

other equipment used in the system.

* 1. The automatic gain control (AGC) indicator LED should be lit confirming a presence of a video signal.
	2. Successful video link operation should be visible at this point as witnessed by a good

quality video picture on the monitor.

* 1. CLEANING
1. Follow all instructions for proper use of solvents and adhesives used for termination and splicing.
2. At completion of the installation, dispose of all

fiber scraps properly.

# MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

# VT72430-R3 SERIES

**DESCRIPTION OPTICAL POWER BUDGET**

**MAXIMUM DISTANCE**

VT72430-R3 SM Video – 1510/1530/1550 >, 1 Fiber, Rack

Mount

10 dB 25 miles (40 km)

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

|  |  |
| --- | --- |
| **VR72430-R3 SERIES** | **DESCRIPTION** |
| VR72430-R3 | SM Video – 1510/1530/1550 > 1 Fiber, Rack Mount |

* Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch

panels.

Table B: Product Compatibility Chart

# TRANSMITTER COMPATIBLE RECEIVER

VT72430-R3 VR72430-R3

# END OF SECTION