DIVISION 28 23 23

VT/VR7400-2DRDT SERIES – FIBER OPTIC TRANSMITTER AND RECEIVER ENGINEERING SPECIFICATIONS

PART 1 - GENERAL

SUMMARY

A.   Fiber Optic Digital 4 Channel Video Multiplexing System with two channels of bi- directional data.

SECTION INCLUDES

VT/VR7420-2DRDT Digital 4 Channel Video Multiplexing System with two channels of bi- directional data.– Standalone

VT/VR7420-2DRDT-R3 Digital 4 Channel Video Multiplexing System with two channels of

bi-directional data.- Rack Mount

VT/VR7430-2DRDT Digital 4 Channel Video Multiplexing System with two channels of bi- directional data.– Standalone

VT/VR7430-2DRDT-R3 Digital 4 Channel Video Multiplexing System with two channels of

bi-directional data.- Rack Mount

VT/VR7830-2DRDT-HP Digital 4 Channel Video Multiplexing System with two channels of bi-directional data.– High power optics Standalone

VT/VR7830-2DRDT-HP-R3 Digital 4 Channel Video Multiplexing System with two channels of bi-directional data.- High power optics Rack Mount

REFERENCES

Underwriters Laboratory (UL)

Underwriters Laboratory Canada (ULC) C.

SYSTEM DESCRIPTION

Performance Requirements: Provide a Digital 4 Channel Video Multiplexing System.

The system shall utilize 1310/1550nm optics

capable of digitally encoding and decoding four channels of video and two channels of bi-directional data on one multimode optical fiber. (VT/VR7420-2DRDT)

The system shall utilize 1310/1550nm optics capable of digitally encoding and decoding four channels of video and two channels of bi-directional data on one single mode optical fiber. (VT/VR7430-2DRDT, VT/VR7430-2DRDT-HP)

SUBMITTALS

Product Data: Manufacturer’s printed product data sheet for each type of Transmitter/Receiver

specified.

Detail Drawings: Electrical and optical connect drawings. Product mounting template.

Manufacturer’s Installation and Operating Manual: Printed installation and operating

information for each type of Transmitter/Receiver specified.

Test Reports: Manufacturer’s Printed Test Report via a Tektronics VM700A Video Test Generator verifying product performance meets or exceeds the specified product performance referenced in Part 2.

Warranty: Manufacturer’s Printed Warranty

DELIVERY, STORAGE AND HANDLING

Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.

Inspect product upon delivery to assure that

specified products have been received.

Store in original packaging in a climate controlled environment. Storage Temperature

not to exceed: -40˚ C to +85˚ C

PROJECT/SITE CONDITIONS

Temperature Requirements: Products shall operate in an environment with an ambient

temperature range of –40˚ C to +74˚ C without

the assistance of fan-forced cooling.

Humidity Requirements: Products shall operate in an environment with relative humidity of 0%

to 95% (non-condensing). If product is installed

in condensation conditions, unit shall have conformal coating applied to the printed circuit board.

WARRANTY

A.   Standard International Fiber Systems Comprehensive Lifetime Warranty: IFS warrants the product to be free of factory defects under manufacture’s Lifetime Warranty as submitted under article 1.05 (E)

PART 2 - PRODUCTS

MANUFACTURER

Acceptable Manufacturer: International Fiber Systems, Inc.; 16 Commerce Road, Newtown,

CT 06470 USA; Telephone: 203-426-1180; Fax

203-426-3326; Email: sales@ifs.com; Internet:

www.ifs.com

Substitutions: Not Permitted

All fiber optic modules shall be supplied from a single manufacturer.

MANUFACTURED UNITS

Model Number Descriptions: Reference Table A: Product Number Descriptions

Model Compatibility Chart: Reference Table B:

Product Compatibility Chart

GENERAL SPECIFICATIONS

A.	The Digital four channel video encoding and decoding system with two channels of bi-directional data shall be an IFS VT/VR7400-2DRDT series module.  The module shall be capable of digitally encoding and decoding four channels of full color video in real time in NTSC, PAL or SECAM formats and two channels of data. The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.  The module shall transmit the video and data using state – of – the – art digital encoding and decoding of the optical signal. The module shall provide power, local video presence, remote video presence, data transmitted

and received and optical carrier detect status indicating LED’s for monitoring proper system operation. The modules shall provide automatic re- settable solid-state current limiters and independent voltage regulators on each module to reduce the chance of a single point failure of the system. The module shall be hot swappable in a rack mount system to reduce complete system shut down during maintenance or repair. The module shall have an MTBF of >100,000 hours and operate in an environment of –40˚ C to +74˚ C and relative humidity between 0% to 95% (non-condensing). The module shall be UL and ULC listed and . The circuit board shall be UL 94 flame rated and meet all PCI standards. All PC boards shall be designated with part number, PC board number and show appropriate revision number. Housing shall be of all metal construction. All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

VIDEO SPECIFICATIONS

Input Video: 1 volt pk-pk (75 ohms)

# of Inputs and Output Channels: 4

Bandwidth: 10 Hz – 6.5 MHz

Differential Gain: < 2 %

Differential Phase: < 0.7 °

Tilt: <1%

Signal/Noise Ratio: 60 dB @ maximum optical loss budget

DATA SPECIFICATIONS

Data Channels:2

Data Format: RS-232, RS-422, 2 or 4 wire RS- 422 with Tri-state Manchester Bi-Phase and Sensornet

Data Rate: DC- 100 kbps (NRZ)

Bit Error Rate: <1 in 10⎯9@ maximum optical

loss budget

Operating Mode: Simplex or Full Duplex

OPTICAL SPECIFICATIONS

IFS Model Number VT/VR7420-2DRDT

Optical Fiber: 62.5/125 micron multimode

Number of Fibers Required: 1

Optical Wavelength: 1310/1550nm

Optical Power Budget: 10 dB

Optical Attenuation: No manual adjustments required

IFS Model Number VT/VR7430-2DRDT

Optical Fiber: 9/125 micron single mode

Number of Fibers Required: 1

Optical Wavelength: 1310/1550nm

Optical Power Budget: 15 dB

Optical Attenuation: No manual adjustments required

IFS Model Number VT/VR7430-2DRDT-HP

Optical Fiber: 9/125 micron single mode

Number of Fibers Required: 1

Optical Wavelength: 1310/1550nm

Optical Power Budget: 20 dB

Optical Attenuation: No manual adjustments required

STATUS INDICATORS

Power: On/Green – Off/Off

Video Input/Output synch for each channel: Video synch/Green – No Video Present/Red

Local and remote video present: Video

present/Green – No Remote Video Present/Red

Data Transmit/Data received: Data TX/RX Green, No Data Red

Optical carrier detect: Detect Green, None Red

CONNECTORS

Optical: ST, SC or FC ( See ordering Information)

Power and Data: Terminal Block with Screw

Clamps

Video: BNC (Gold Plated Center-PIN)

ELECTRICAL SPECIFICATIONS

Power: 12 VDC@ 500ma (stand-alone)

Current Protection: Automatic re-settable solid- state current limiters

Voltage Regulation: Solid-state, Independent on each board

Circuit Board: UL 94 flame rated and meets all PCI standards.

Rack mount Card: Shall be hot-swappable with IFS Model Number R3 (EIA 19” card cage)

MECHANICAL SPECIFICATIONS

Surface Mount Dimensions: 7.0” x 4.9” x 2.0”

(17.8 cm x 12.5 cm x 5.1 cm)

Rack Mount Dimensions: 7.7” x 5.0” x 3.0”

(19.6 cm x 12.7 cm x 7.6 cm)

Number of Rack Slots: 4

Finish: Module shall be constructed of a metal enclosure with a powder coat finish model Number F63B12 with all connections and indicators silk-screened directly on unit. Rack mount units shall be constructed of anodized aluminum.

Weight: <2.0 lbs./0.9kg

ENVIRONMENTAL SPECIFICATIONS

MTBF: >100,000 Hours

Operating Temp: –40˚ C to +74˚ C

Storage Temp: -40˚ C to +85˚ C

Relative Humidity: 0% to 95% (non- condensing). If product is installed under

condensation conditions, unit shall have

conformal coating applied to the printed circuit board. (Add –C to model number for conformal coated printed circuit board)

REGULATORY AGENCIES/APPROVALS AND LISTINGS

Underwriters Laboratory (UL) Listing Number:

I.T.E. 6D16

Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

UL 94-flame rated PCB board: 94VO D.

ACCESSORIES

Card Cage: IFS Model Number R3 (EIA 19” card cage) shall be available to house and power rack mount modules.

Blank Panels: IFS Model Number R3-BP shall be available to cover unused rack slots.

PART 3 - EXECUTION

EXAMINATION

Inspect modules before installation.

Modules shall be free of any cosmetic defects or damage.

All optical connectors shall be covered with dust caps and remain on the module until installing

cable connectors to module.

Shipping box shall include the module, power supply and operations manual.

PREPARATION

Standalone Module (Surface Mount)

Shall be mounted on a properly prepared surface adequate for the size and weight of

module. The placement of the unit shall

allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the IFS mounting template and installation manual.

Rack Mount Module (19” Rack)

Shall be installed in the IFS Model Number R3 card cage. Ensure the card cage is installed in a standard EIA 19” (482.6 mm) rack or wall standoff bracket adequate for the size and weight of the card cage. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the IFS installation manual.

Optical Fibers

Caution: NEVER look into the end of an active optical fiber when using laser light

output. Eye damage can occur. Wear eye

protection when cleaving, terminating, and splicing fiber.

The number and type (multimode or single- mode) of optical fiber shall meet the requirements of the IFS model number in article 2.05 used in the installation.

All optical fiber cables shall be properly installed and terminated with the mating optical connectors as submitted in article

2.07 (A).

The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.05.

All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

INSTALLATION

A.   General: Locate fiber optic modules as indicated on the approved detail drawings and install

module in compliance with the IFS installation and operations manual.

TESTING

Testing the Fiber Optic Video Link.

Verify that the coax and optic fibers are properly connected.

Make sure that power is applied to all fiber optic modules, camera, and video monitor or

other equipment used in the system.

The automatic gain control (AGC) indicator LED should be lit confirming a presence of

a video signal.

Successful video link operation should be visible at this point as witnessed by a good quality video picture on the monitor.

CLEANING

Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

At completion of the installation, dispose of all fiber scraps properly.

MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

| VT7400-2DRDT SERIES | DESCRIPTION | OPTICAL POWER BUDGET | MAXIMUM DISTANCE |
| --- | --- | --- | --- |
| VT7420-2DRDT | MM Video/Data – 1300/1550 >, 1 Fiber | 12 dB | 0.63 miles (1 km) |
| VT7420-2DRDT -R3 | MM Video/Data – 1300/1550 >, 1 Fiber, Rack Mount | 12 dB | 0.63 miles (1 km) |
| VT7430-2DRDT | SM Video/Data – 1300/1550 >, 1 Fiber | 20 dB | 37 miles (60 km) |
| VT7430-2DRDT -R3 | SM Video/Data– 1300/1550 >, 1 Fiber, Rack Mount | 20 dB | 37 miles (60 km) |
| VT7430-2DRDT-HP | SM Video/Data – 1300/1550 >, 1 Fiber | 26 dB | 49 miles (78 km) |
| VT7430-2DRDT -HP-R3 | SM Video/Data – 1300/1550 >, 1 Fiber, Rack Mount | 26 dB | 49 miles (78 km) |

Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch

panels.

VR7400-2DRDT SERIES	DESCRIPTION

VR7420	MM Video/Data – 1300/1550 >, 1 Fiber

VR7420-2DRDT -R3	MM Video/Data – 1300/1550 >, 1 Fiber, Rack Mount VR7430-2DRDT	SM Video/Data – 1300/1550 >, 1 Fiber

VR7430-2DRDT -R3	SM Video/Data– 1300/1550 >, 1 Fiber, Rack Mount VR7430-2DRDT-HP	SM Video/Data – 1300/1550 >, 1 Fiber

VR7430-2DRDT –HP-R3	SM Video/Data – 1300/1550 >, 1 Fiber, Rack Mount

Maximum distance is limited to optical loss of the fiber and any additional loss by connectors, splices and patch panels.

Table B: Product Compatibility Chart

TRANSMITTER	COMPATIBLE RECEIVER

VT7420-2DRDT	VR7420-2DRDT, VR7820-2DRDT -R3

VT7420-2DRDT -R3	VR7420-2DRDT, VR7820-2DRDT -R3

VT7430-2DRDT	VR7430-2DRDT, VR7830-2DRDT -R3

VT7430-2DRDT -R3	VR7430-2DRDT, VR7830-2DRDT -R3

VT7430-2DRDT-HP	VR7430-2DRDT-HP, VR7430-2DRDT –HP-R3

VT7430-2DRDT -HP-R3	VR7430-2DRDT-HP, VR7430-2DRDT –HP-R3

END OF SECTION