DIVISION 28 23 23

VR1000 SERIES – FIBER OPTIC RECEIVER ENGINEERING SPECIFICATIONS

PART 1 - GENERAL

SUMMARY

A.   Fiber Optic AM Video Receiver

SECTION INCLUDES

A.   VR1000 Series AM Video Receiver – Standalone

REFERENCES

Underwriters Laboratory (UL)

Underwriters Laboratory Canada (ULC)

European Union Compliance (CE)

SYSTEM DESCRIPTION

Performance Requirements: Provide an AM Video Receiver.

The system shall utilize an 850nm optic capable of receiving video on one

multimode optical fiber. (VR1000)

SUBMITTALS

Product Data: Manufacturer’s printed product data sheet for each type of Transmitter/Receiver specified.

Detail Drawings: Electrical and optical connect drawings. Product mounting template.

Manufacturer’s Installation and Operating

Manual: Printed installation and operating information for each type of Transmitter/Receiver specified.

Test Reports: Manufacturer’s Printed Test Report via a Tektronics VM700A Video Test

Generator verifying product performance meets

or exceeds the specified product performance referenced in Part 2.

Warranty: Manufacturer’s Printed Warranty

DELIVERY, STORAGE AND HANDLING

Deliver materials in unopened factory packaging with Manufacturer’s bar coding to the job site.

Inspect product upon delivery to assure that specified products have been received.

Store in original packaging in a climate controlled environment. Storage Temperature

not to exceed: -40˚ C to +85˚ C

PROJECT/SITE CONDITIONS

Temperature Requirements: Products shall operate in an environment with an ambient temperature range of –40˚ C to +74˚ C without the assistance of fan-forced cooling.

Humidity Requirements: Products shall operate in an environment with relative humidity of 0% to 95% (non-condensing). If product is installed in condensation conditions, unit shall have conformal coating applied to the printed circuit board.

WARRANTY

A.   Standard International Fiber Systems Comprehensive Lifetime Warranty: IFS

warrants the product to be free of factory defects

under manufacture’s Lifetime Warranty as submitted under article 1.05 (E)

PART 2 - PRODUCTS

MANUFACTURER

Acceptable Manufacturer: International Fiber Systems, Inc.; 16 Commerce Road, Newtown,

CT 06470 USA; Telephone: 203-426-1180; Fax

203-426-3326; Email: sales@ifs.com; Internet:

www.ifs.com

Substitutions: Not Permitted

All fiber optic modules shall be supplied from a single manufacturer.

MANUFACTURED UNITS

Model Number Descriptions: Reference Table A: Product Number Descriptions

Model Compatibility Chart: Reference Table B: Product Compatibility Chart

GENERAL SPECIFICATIONS

A.   The AM Video Receiver shall be an IFS VR1000 series module. The module shall be capable of

receiving full color video in real time in NTSC,

PAL or SECAM formats.  The module shall  have user accessible manual gain control for video adjustment. The module shall require no in-line attenuators to ease installation.  The module shall provide a power status indicating LED for monitoring proper system operation. The modules shall provide automatic re-settable solid-state current limiters and independent voltage regulators on each module to reduce the chance of a single point failure of the system. The module shall have an MTBF of >100,000 hours and operate in an environment of –40˚ C to

+74˚ C and relative humidity between 0% to  95% (non-condensing). The module shall be UL and ULC listed and CE marked. The circuit board shall be UL 94 flame rated and meet all PCI standards. All PC boards shall be  designated with part number, PC board number and show appropriate revision number. Housing shall be of all metal construction. All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels. The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

VIDEO SPECIFICATIONS

Output Video: 1 volt pk-pk (75 ohms)

Bandwidth: 5 Hz – 10 MHz

Differential Gain: < 5 %.

Differential Phase: < 5 °.

Tilt: <1%

Signal/Noise Ratio: 60dB

OPTICAL SPECIFICATIONS

IFS Model Number VR1000

Optical Fiber: 62.5/125 micron multimode

Number of Fibers Required: 1

Optical Wavelength: 850nm

Optical Receiver Type: 850nm PIN Diode

Project name/project number/date	00000 - 1	Section Title (Optional information, e.g., owner, A/E)

Optical Attenuation: No manual adjustments required

STATUS INDICATORS

A.   Power: On/Red – Off/Off

CONNECTORS

Optical: ST

Power: Terminal Block with Screw Clamps

Video: BNC (Gold Plated Center-PIN)

ELECTRICAL SPECIFICATIONS

Power: 12VDC

Current Protection: Automatic re-settable solid- state current limiters

Voltage Regulation: Solid-state, Independent on each board

Circuit Board: UL 94 flame rated and meets all PCI standards.

MECHANICAL SPECIFICATIONS

Surface Mount Dimensions: 4.2” x 3.5” x 1.0”

(10.67 cm x 8.90 cm x 2.54 cm)

Finish: Module shall be constructed of a metal enclosure with a powder coat finish model

Number F63B12 with all connections and

indicators silk-screened directly on unit. Rack mount units shall be constructed of anodized aluminum.

Weight: <2.0 lbs./1.0kg

ENVIRONMENTAL SPECIFICATIONS

MTBF: >100,000 Hours

Operating Temp: –40˚ C to +74˚ C

Storage Temp: -40˚ C to +85˚ C

Relative Humidity: 0% to 95% (non- condensing). If product is installed under condensation conditions, unit shall have conformal coating applied to the printed circuit board. (Add –C to model number for conformal coated printed circuit board)

REGULATORY AGENCIES/APPROVALS AND LISTINGS

Underwriters Laboratory (UL) Listing Number:

I.T.E. 6D16

Underwriters Laboratory Canada (ULC) Listing Number: I.T.E. 6D16

UL 94-flame rated PCB board: 94VO D.

ACCESSORIES

PART 3 - EXECUTION

EXAMINATION

Inspect modules before installation.

Modules shall be free of any cosmetic defects or damage.

All optical connectors shall be covered with dust

caps and remain on the module until installing cable connectors to module.

Shipping box shall include the module, power supply and operations manual.

PREPARATION

Standalone Module (Surface Mount)

Shall be mounted on a properly prepared surface adequate for the size and weight of module. The placement of the unit shall allow provision for cable installation and maintenance as indicated on the approved detail drawings and in compliance with the IFS mounting template and installation manual.

Optical Fibers

Caution: NEVER look into the end of an active optical fiber when using laser light

output. Eye damage can occur. Wear eye

protection when cleaving, terminating, and splicing fiber.

The number and type (multimode or single- mode) of optical fiber shall meet the

requirements of the IFS model number in article 2.05 used in the installation.

All optical fiber cables shall be properly installed and terminated with the mating

optical connectors as submitted in article

2.07 (A).

The optical link shall be tested with either a power meter, at a minimum, or OTDR to ensure the link budget (overall path loss) plus an added 3dB of optical safety margin does not exceed the optical power budget as submitted in article 2.05.

All optical connectors on cable shall be cleaned in compliance to optical connector manufactures specifications and covered with dust caps until connection to the fiber optic module.

INSTALLATION

A.   General: Locate fiber optic modules as indicated on the approved detail drawings and install module in compliance with the IFS installation and operations manual.

TESTING

Testing the Fiber Optic Video Link.

Verify that the coax and optic fibers are properly connected.

Make sure that power is applied to all fiber optic modules, camera, and video monitor or

other equipment used in the system.

Successful video link operation should be visible at this point as witnessed by a good

quality video picture on the monitor.

CLEANING

Follow all instructions for proper use of solvents and adhesives used for termination and splicing.

At completion of the installation, dispose of all

fiber scraps properly.

Section Title	00000 - 2		Project name/project number/date (Optional information, e.g., owner, A/E)

MANUFACTURED UNITS REFERENCE TABLES

Table A: Product Number Descriptions

VR1000 SERIES	DESCRIPTION

VR1000	MM Video – 850 > 1 Fiber

Table B: Product Compatibility Chart

RECEIVER	COMPATIBLE TRANSMITTERS

VR1000	VT1101M, VT1000AC, VT1001, VT1001-R3

END OF SECTION

Project name/project number/date	00000 - 3	Section Title (Optional information, e.g., owner, A/E)